## Overview
Tab | Contents | Colour coding in the tab
Full map Auto | A list of all Modbus registers | Currently used | Suggested, preferrably don't change | Suggested, can be changed
Green text = Obsolete register
Red text = Value fetched from "Channel data etc" tab
Channel data etc | Description of contents in "channel based values" such as Load profile, Previous values and demand | Currently used | Grey text = Reserved but not used yet | Suggested, can be changed
Configuration | Procedure for reading/writing tariff configuration
ModCom map Auto | Modbus registers used in ModCom
Sace analyzer | Observations from testing a Sace analyzer, when developing ModCom. Still useful/valid?
Note! Be careful when changing register addresses in the mapping. Many of them are calculated automatically based on other cells
For example check that the "SUM" and "Control (DEC)" fields match.

## Full map Auto
Category |  | Sub-categories | Details 1 | Details 2 | Register(s) | Reg (Dec) | Nr of quantities | Size | Nr of registers | Base register (Hex) | Base register (dec) | Min | Max | Resolution | Unit | Min | Max | Type
Energies | Total | Active imp | kWh |  | 5000 | 20480 | 1 | 4 | 4 | 5000 | 20480 | 0 | 1.8447e+19 | 0.01 | kWh | 0.00 | 1.8447e+17 | Unsigned
(Read only) |  | Active exp | kWh |  | 5004 | 20484 | 1 | 4 | 4 |  |  | 0 | 1.8447e+19 | 0.01 | kWh | 0.00 | 1.8447e+17 | Unsigned
|  | Active net | kWh |  | 5008 | 20488 | 1 | 4 | 4
|  | Reactive imp | kvarh |  | 500C | 20492 | 1 | 4 | 4 |  |  | 0 | 1.8447e+19 | 0.01 | kvarh | 0.00 | 1.8447e+17 | Unsigned
|  | Reactive exp | kvarh |  | 5010 | 20496 | 1 | 4 | 4 |  |  | 0 | 1.8447e+19 | 0.01 | kvarh | 0.00 | 1.8447e+17 | Unsigned
|  | Reactive net | kvarh |  | 5014 | 20500 | 1 | 4 | 4
|  | Apparent imp | kVA |  | 5018 | 20504 | 1 | 4 | 4
|  | Apparent exp | kVA |  | 501C | 20508 | 1 | 4 | 4
|  | Apparent net | kVA |  | 5020 | 20512 | 1 | 4 | 4
|  | Active imp | CO2 |  | 5024 | 20516 | 1 | 4 | 4
|  | Active exp | CO2 |  | 5028 | 20520 | 1 | 4 | 4
|  | Reactive imp | CO2 |  | 502C | 20524 | 1 | 4 | 4
|  | Reactive exp | CO2 |  | 5030 | 20528 | 1 | 4 | 4
|  | Active imp | Currency |  | 5034 | 20532 | 1 | 4 | 4
|  | Active exp | Currency |  | 5038 | 20536 | 1 | 4 | 4
|  | Reactive imp | Currency |  | 503C | 20540 | 1 | 4 | 4
|  | Reactive exp | Currency |  | 5040 | 20544 | 1 | 4 | 4
Capacitive/Inductive? (Sace has that, split up into tariffs)
|  | Reserved |  |  | 5044 | 20548 |  | 300 | 300
| Tariffs | Active imp | kWh | Tariff 1..8 | 5170 | 20848 | 8 | 4 | 32 |  |  | 0 | 1.8447e+19 | 0.01 | kWh | 0.00 | 1.8447e+17 | Unsigned
|  | Active exp | kWh | Tariff 1..8 | 5190 | 20880 | 8 | 4 | 32
|  | Reactive imp | kvarh | Tariff 1..8 | 51B0 | 20912 | 8 | 4 | 32 |  |  | 0 | 1.8447e+19 | 0.01 | kvarh | 0.00 | 1.8447e+17 | Unsigned
|  | Reactive exp | kvarh | Tariff 1..8 | 51D0 | 20944 | 8 | 4 | 32
|  | Apparent imp | kVAh | Tariff 1..8 | 51F0 | 20976 | 8 | 4 | 32
|  | Apparent exp | kVAh | Tariff 1..8 | 5210 | 21008 | 8 | 4 | 32
|  | Active imp | CO2 | Tariff 1..8 | 5230 | 21040 | 8 | 4 | 32
|  | Active exp | CO2 | Tariff 1..8 | 5250 | 21072 | 8 | 4 | 32
|  | Reactive imp | CO2 | Tariff 1..8 | 5270 | 21104 | 8 | 4 | 32
|  | Reactive exp | CO2 | Tariff 1..8 | 5290 | 21136 | 8 | 4 | 32
|  | Active imp | Currency | Tariff 1..8 | 52B0 | 21168 | 8 | 4 | 32
|  | Active exp | Currency | Tariff 1..8 | 52D0 | 21200 | 8 | 4 | 32
|  | Reactive imp | Currency | Tariff 1..8 | 52F0 | 21232 | 8 | 4 | 32
|  | Reactive exp | Currency | Tariff 1..8 | 5310 | 21264 | 8 | 4 | 32
|  | Reserved |  |  | 5330 | 21296 |  | 304 | 304
| Phases | Active imp | kWh | L1..L3 | 5460 | 21600 | 3 | 4 | 12
|  | Active exp | kWh | L1..L3 | 546C | 21612 | 3 | 4 | 12
|  | Active net | kWh | L1..L3 | 5478 | 21624 | 3 | 4 | 12
|  | Reactive imp | kvarh | L1..L3 | 5484 | 21636 | 3 | 4 | 12
|  | Reactive exp | kvarh | L1..L3 | 5490 | 21648 | 3 | 4 | 12
|  | Reactive net | kvarh | L1..L3 | 549C | 21660 | 3 | 4 | 12
|  | Apparent imp | kVA | L1..L3 | 54A8 | 21672 | 3 | 4 | 12
|  | Apparent exp | kVA | L1..L3 | 54B4 | 21684 | 3 | 4 | 12
|  | Apparent net | kVA | L1..L3 | 54C0 | 21696 | 3 | 4 | 12
|  | Active imp | CO2 | L1..L3 | 54CC | 21708 | 3 | 4 | 12
|  | Active exp | CO2 | L1..L3 | 54D8 | 21720 | 3 | 4 | 12
|  | Reactive imp | CO2 | L1..L3 | 54E4 | 21732 | 3 | 4 | 12
|  | Reactive exp | CO2 | L1..L3 | 54F0 | 21744 | 3 | 4 | 12
|  | Active imp | Currency | L1..L3 | 54FC | 21756 | 3 | 4 | 12
|  | Active exp | Currency | L1..L3 | 5508 | 21768 | 3 | 4 | 12
|  | Reactive imp | Currency | L1..L3 | 5514 | 21780 | 3 | 4 | 12
|  | Reactive exp | Currency | L1..L3 | 5520 | 21792 | 3 | 4 | 12
| Resettable | Active import total | kWh |  | 552C | 21804 | 1 | 4 | 4
|  | Active export total | kWh |  | 5530 | 21808 | 1 | 4 | 4
|  | Reactive import total | kvarh |  | 5534 | 21812 | 1 | 4 | 4
|  | Reactive export total | kvarh |  | 5538 | 21816 | 1 | 4 | 4
| Ph/Tariff | Active imp | kWh | L1..L3, tar 1..8 | 553C | 21820 | 24 | 4 | 96
|  | Active exp | kWh | L1..L3, tar 1..8 | 559C | 21916 | 24 | 4 | 96
|  | Reactive imp | kvarh | L1..L3, tar 1..8 | 55FC | 22012 | 24 | 4 | 96
|  | Reactive exp | kvarh | L1..L3, tar 1..8 | 565C | 22108 | 24 | 4 | 96
|  | Apparent imp | kVA | L1..L3, tar 1..8 | 56BC | 22204 | 24 | 4 | 96
|  | Apparent exp | kVA | L1..L3, tar 1..8 | 571C | 22300 | 24 | 4 | 96
|  | Active imp | CO2 | L1..L3, tar 1..8 | 577C | 22396 | 24 | 4 | 96
|  | Active exp | CO2 | L1..L3, tar 1..8 | 57DC | 22492 | 24 | 4 | 96
|  | Reactive imp | CO2 | L1..L3, tar 1..8 | 583C | 22588 | 24 | 4 | 96
|  | Reactive exp | CO2 | L1..L3, tar 1..8 | 589C | 22684 | 24 | 4 | 96
|  | Active imp | Currency | L1..L3, tar 1..8 | 58FC | 22780 | 24 | 4 | 96
|  | Active exp | Currency | L1..L3, tar 1..8 | 595C | 22876 | 24 | 4 | 96
|  | Reactive imp | Currency | L1..L3, tar 1..8 | 59BC | 22972 | 24 | 4 | 96
|  | Reactive exp | Currency | L1..L3, tar 1..8 | 5A1C | 23068 | 24 | 4 | 96
|  | Reserved |  |  | 54A8 | 21672 |  | 132 | 132
[9 empty] | Sum |  | Control (Dec)
Sum | [6 empty] | 520 |  | 2816 | B00 | 2816
Instantaneous |  | Voltages | L1..L3 |  | 5B00 | 23296 | 3 | 2 | 6 | 5B00 | 23296 | 0 | 4294967295 | 0.1 | V | 0.0 | 429496729.5 | Unsigned
(Read only) |  |  | L1-L2 |  | 5B06 | 23302 | 1 | 2 | 2 |  |  | 0 | 4294967295 | 0.1 | V | 0.0 | 429496729.5 | Unsigned
|  |  | L3-L2 |  | 5B08 | 23304 | 1 | 2 | 2 |  |  | 0 | 4294967295 | 0.1 | V | 0.0 | 429496729.5 | Unsigned
|  |  | L1-L3 |  | 5B0A | 23306 | 1 | 2 | 2 |  |  |  |  | 0.1
|  | Currents | L1..L3, N |  | 5B0C | 23308 | 4 | 2 | 8 |  |  | -2147483648 | 2147483647 | 0.001 | A | 0.00 | 4294967.295 | Unsigned
|  | Powers | Active | Total, L1..L3 | 5B14 | 23316 | 4 | 2 | 8 |  |  | -2147483648 | 2147483647 | 0.01 | W | -21474836.48 | 21474836.47 | Signed
|  | Total, i.e. imp-exp | Reactive | Total, L1..L3 | 5B1C | 23324 | 4 | 2 | 8 |  |  | -2147483648 | 2147483647 | 0.01 | var | -21474836.48 | 21474836.47 | Signed
|  |  | Apparent | Total, L1..L3 | 5B24 | 23332 | 4 | 2 | 8 |  |  | -2147483648 | 2147483647 | 0.01 | VA | -21474836.48 | 21474836.47 | Signed
|  | Frequency |  |  | 5B2C | 23340 | 1 | 1 | 1 |  |  | 0 | 65535 | 0.01 | Hz | 0.00 | 655.35 | Unsigned
|  | Phase angles | Power | Total, L1..L3 | 5B2D | 23341 | 4 | 1 | 4 |  |  | 0 | 65535 | 0.1 | ° | -3276.8 | 3276.7 | Signed
|  |  | Voltage | L1..L3 | 5B31 | 23345 | 3 | 1 | 3 |  |  | 0 | 65535 | 0.1 | ° | -3276.8 | 3276.7 | Signed
|  |  |  | L1-L2 | 5B34 | 23348 | 1 | 1 | 1
|  |  |  | L3-L2 | 5B35 | 23349 | 1 | 1 | 1
|  |  |  | L1-L3 | 5B36 | 23350 | 1 | 1 | 1
|  |  | Current | L1..L3 | 5B37 | 23351 | 3 | 1 | 3 |  |  | 0 | 65535 | 0.1 | ° | -3276.8 | 3276.7 | Signed
|  | Power factors |  | Total, L1..L3 | 5B3A | 23354 | 4 | 1 | 4 |  |  | 0 | 65535 | 0.001 | - | -32.768 | 32.767 | Signed
|  | Current quadrant |  | Total, L1..L3 | 5B3E | 23358 | 4 | 1 | 4 |  |  | 0 | 65535 | Quadrant nr (1-4) |  | 0 | 65535 | Unsigned
|  | Crest factor | L1..L3?
Current/Voltage unbalance
Phase sequece
|  | Reserved |  |  | 5B42 | 23362 |  | 446 | 446
|  | Voltage harmonics | L1 (THD,2nd,3rd…) | 1..128 | 5D00 | 23808 | 128 | 1 | 128
|  |  | L2 (THD,2nd,3rd…) | 1..128 | 5D80 | 23936 | 128 | 1 | 128
|  |  | L3 (THD,2nd,3rd…) | 1..128 | 5E00 | 24064 | 128 | 1 | 128
|  |  | L1-L2 (THD,2nd,3rd) | 1..128 | 5E80 | 24192 | 128 | 1 | 128
|  |  | L3-L2 (THD,2nd,3rd) | 1..128 | 5F00 | 24320 | 128 | 1 | 128
|  |  | L1-L3 (THD,2nd,3rd) | 1..128 | 5F80 | 24448 | 128 | 1 | 128
|  | Current harmonics | L1 (THD,2nd,3rd…) | 1..128 | 6000 | 24576 | 128 | 1 | 128
|  |  | L2 (THD,2nd,3rd…) | 1..128 | 6080 | 24704 | 128 | 1 | 128
|  |  | L3 (THD,2nd,3rd…) | 1..128 | 6100 | 24832 | 128 | 1 | 128
|  |  | N (THD,2nd,3rd…) | 1..128 | 6180 | 24960 | 128 | 1 | 128
|  | All harmonics (voltage) | L1..L3 |  | 6200 | 25088 | 3 | 1 | 3
|  |  | L1-L2 |  | 6203 | 25091 | 1 | 1 | 1
|  |  | L3-L2 |  | 6204 | 25092 | 1 | 1 | 1
|  |  | L1-L3 |  | 6205 | 25093 | 1 | 1 | 1
|  | All harmon. to nominal value ratio | L1..L3 |  | 6206 | 25094 | 3 | 1 | 3
|  |  | L1-L2 |  | 6209 | 25097 | 1 | 1 | 1
|  |  | L3-L2 |  | 620A | 25098 | 1 | 1 | 1
|  |  | L1-L3 |  | 620B | 25099 | 1 | 1 | 1
|  | Reserved |  |  | 620C | 25100 |  | 4 | 4
|  | All harmonics (current) | L1..L3, N |  | 6210 | 25104 | 4 | 4 | 16
|  | All harmon. to nominal value ratio | L1..L3, N |  | 6220 | 25120 | 4 | 4 | 16
|  | Reserved |  |  | 6230 | 25136 |  | 16 | 16
15 min averages |  | Generic average channels |  |  | 6240 | 25152 |  | 10 | 10
|  | Reserved |  |  | 624A | 25162 |  | 182 | 182
[9 empty] | Sum |  | Control (Dec)
Sum | [6 empty] | 1344 |  | 2048 | 800 | 2048
I/O |  | Outputs | Output 1..8 | (1 Reg each) | 6300 | 25344 | 8 | 1 | 8 | 6300 | 25344 | 0 | 1 | ON/OFF | - | 0 | 65535 | Unsigned
(Read/Write) |  | Inputs | Input 1..8 | (1 Reg each) | 6308 | 25352 | 8 | 1 | 8 |  |  | 0 | 1 | ON/OFF | - | 0 | 65535 | Unsigned
|  | Stored inputs | Input 1..8 | (1 Reg each) | 6310 | 25360 | 8 | 1 | 8 |  |  | 0 | 1 | ON/OFF | - | 0 | 65535 | Unsigned
|  | Counters | Input 1..8 | (4 Regs each) | 6318 | 25368 | 8 | 4 | 32 |  |  | 0 | 1.8447e+19 | - | - | 0 | 1.8447e+19 | Unsigned
|  | Analogue outputs | Analogue 1..16 |  | 6338 | 25400 | 16 | 4 | 64
|  | Analogue inputs | Analogue 1..16 |  | 6378 | 25464 | 16 | 4 | 64
|  | Reserved |  |  | 63B8 | 25528 |  | 328 | 328
[9 empty] | Sum |  | Control (Dec)
Sum | [6 empty] | 64 |  | 512 | 200 | 512
Event log |  | System log |  |  | 6500 | 25856 |  | 121 | 121 | 6500 | 25856
(Read/Write) |  | Reserved |  |  | 6579 | 25977 |  | 55 | 55
|  | Event log |  |  | 65B0 | 26032 |  | 121 | 121
|  | Reserved |  |  | 6629 | 26153 |  | 55 | 55
|  | Audit log |  |  | 6660 | 26208 |  | 121 | 121
|  | Reserved |  |  | 66D9 | 26329 |  | 55 | 55
|  | Net Quality log |  |  | 6710 | 26384 |  | 121 | 121
|  | Reserved |  |  | 6789 | 26505 |  | 55 | 55
|  | Comm log |  |  | 67C0 | 26560 |  | 121 | 121
|  | Reserved |  |  | 6839 | 26681 |  | 199 | 199
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 1024 | 400 | 1024
Waveform capture |  | Voltage | L1 |  | 6900 | 26880 | 256 | 2 | 512 | 6900 | 26880
(Read only) |  |  | L2 |  | 6B00 | 27392 | 256 | 2 | 512
|  |  | L3 |  | 6D00 | 27904 | 256 | 2 | 512
|  |  | L1-L2 |  | 6F00 | 28416 | 256 | 2 | 512
|  |  | L3-L2 |  | 7100 | 28928 | 256 | 2 | 512
|  |  | L1-L3 |  | 7300 | 29440 | 256 | 2 | 512
|  | Current | L1 |  | 7500 | 29952 | 256 | 2 | 512
|  |  | L2 |  | 7700 | 30464 | 256 | 2 | 512
|  |  | L3 |  | 7900 | 30976 | 256 | 2 | 512
|  |  | N |  | 7B00 | 31488 | 256 | 2 | 512
|  | Reserved |  |  | 7D00 | 32000 |  | 512 | 512
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 5632 | 1600 | 5632
Tariff accumulators |  | Generic tariff channels | 8 channels |  | 7F00 | 32512 |  | 70 | 70 | 7F00 | 32512
(Read/Write) |  | Reserved |  |  | 7F46 | 32582 |  | 186 | 186
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 256 | 100 | 256
Previous values |  | Energies, Input counters | Control block |  | 8000 | 32768 |  | 9 | 9 | 8000 | 32768 |  |  | Same resolution etc as for respective quantity |  |  |  | Variable
(Read/Write) |  | Reserved |  |  | 8009 | 32777 |  | 7 | 7
|  |  | Data block 1 |  | 8010 | 32784 |  | 83 | 83 |  |  |  |  | Same resolution etc as for respective quantity |  |  |  | Variable
|  | Reserved |  |  | 8063 | 32867 |  | 13 | 13
|  |  | Data block 2 |  | 8070 | 32880 |  | 83 | 83
|  | Reserved |  |  | 80C3 | 32963 |  | 13 | 13
|  |  | Data block 3 |  | 80D0 | 32976 |  | 83 | 83 |  |  |  |  | Same resolution etc as for respective quantity |  |  |  | Variable
|  | Reserved |  |  | 8123 | 33059 |  | 13 | 13
|  |  | Data block 4 |  | 8130 | 33072 |  | 83 | 83
|  | Reserved |  |  | 8183 | 33155 |  | 13 | 13
|  |  | Data block 5 |  | 8190 | 33168 |  | 83 | 83
|  | Reserved |  |  | 81E3 | 33251 |  | 13 | 13
|  |  | Data block 6 |  | 81F0 | 33264 |  | 83 | 83
|  | Reserved |  |  | 8243 | 33347 |  | 13 | 13
|  |  | Data block 7 |  | 8250 | 33360 |  | 83 | 83
|  | Reserved |  |  | 82A3 | 33443 |  | 93 | 93
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 768 | 300 | 768
Demand |  | Min/Max | Control block |  | 8300 | 33536 |  |  | 11 | 8300 | 33536
|  | Reserved |  |  | 830B | 33547 |  | 5 | 5
|  |  | Data block 1 |  | 8310 | 33552 |  | 115 | 115
|  | Reserved |  |  | 8383 | 33667 |  | 13 | 13
|  |  | Data block 2 |  | 8390 | 33680 |  | 115 | 115
|  | Reserved |  |  | 8403 | 33795 |  | 13 | 13
|  |  | Data block 3 |  | 8410 | 33808 |  | 115 | 115
|  | Reserved |  |  | 8483 | 33923 |  | 13 | 13
|  |  | Data block 4 |  | 8490 | 33936 |  | 115 | 115
|  | Reserved |  |  | 8503 | 34051 |  | 13 | 13
|  |  | Data block 5 |  | 8510 | 34064 |  | 115 | 115
|  | Reserved |  |  | 8583 | 34179 |  | 13 | 13
|  |  | Data block 6 |  | 8590 | 34192 |  | 115 | 115
|  | Reserved |  |  | 8603 | 34307 |  | 13 | 13
|  |  | Data block 7 |  | 8610 | 34320 |  | 115 | 115
|  | Reserved |  |  | 8683 | 34435 |  | 13 | 13
(Read/Write) |  | Cumulative
Coincident
Predicted
Previous
Current
|  | Reserved |  |  | 8690 | 34448 |  | 112 | 112
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 1024 | 400 | 1024
Load profiles |  | Load profile |  |  | 8700 | 34560 |  | 152 | 152 | 8700 | 34560
(Read/Write) |  | Reserved |  |  | 8798 | 34712 |  | 360 | 360
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 512 | 200 | 512
Production data |  | Serial number(s) |  |  | 8900 | 35072 | 1 | 2 | 2 | 8900 | 35072 |  |  | - | - | 0 | 4294967295 | Unsigned
|  | Reserved |  |  | 8902 | 35074 |  | 6 | 6
and identification |  | Meter firmware version |  |  | 8908 | 35080 | 1 | 8 | 8 |  |  |  |  | - | - | 16 characters |  | String
(Read only) |  | Modbus mapping version |  |  | 8910 | 35088 | 1 | 1 | 1 |  |  | 0 | 255 | Major.Minor version |  | 0.0 | 255.255 | 2 bytes
|  | ModCom firmware version |  |  | 8911 | 35089 | 1 | 8 | 8 |  |  |  |  | - | - | 16 characters |  | String
|  | Hardware version(s) | Up to 8 boards (now 3 are used) |  | 8919 | 35097 | 8 | 8 | 64 |  |  |  |  | - | - | 16 characters |  | String
|  | Reserved |  |  | 8959 | 35161 |  | 7 | 7
|  | Type designation | E.g. A43 552-100 |  | 8960 | 35168 | 1 | 6 | 6 |  |  |  |  | - | - | 12 characters |  | String
|  | Logical device name | E.g. ABBEM00000012345 |  | 8966 | 35174 | 1 | 8 | 8
|  | Reserved |  |  | 896E | 35182 |  | 146 | 146
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 256 | 100 | 256
Other |  | Date Time | YYMMDD:HHMMSS | Read/Write | 8A00 | 35328 | 1 | 3 | 3 | 8A00 | 35328 |  |  |  |  | 6 bytes: YYMMDD:HHMMSS |  | DateTime
(Read/Write) |  | Day of week |  |  | 8A03 | 35331 | 1 | 1 | 1 |  |  | 0 | 65535 | Weekday (1-7) |  | 0 | 65535 | Unsigned
|  | DST active |  |  | 8A04 | 35332 | 1 | 1 | 1 |  |  | 0 | 65535 | Enabl./Disabl. (0 / 1) |  | 0 | 65535 | Unsigned
|  | Active day type |  | Read only | 8A05 | 35333 | 1 | 1 | 1 |  |  | 0 | 65535 | Day type |  | 0 | 65535 | Unsigned
|  | Active season |  | Read only | 8A06 | 35334 | 1 | 1 | 1 |  |  | 0 | 65535 | Season type |  | 0 | 65535 | Unsigned
|  | Current tariff (1-4) | Quantity 1..8 | Read/Write | 8A07 | 35335 | 8 | 1 | 8 |  |  | 0 | 65535 | Tariff 1-8 |  | 0 | 65535 | Unsigned
|  | Error flags (old meters) | 64 bit | Read only | 8A0F | 35343 | 1 | 4 | 4 |  |  | 0 | 1 | ON/OFF |  | 64 bits |  | Bit String
|  | Error flags (new meters) | 64 bits | Read only | 8A13 | 35347 | 1 | 4 | 4
|  | Reserved |  |  | 8A17 | 35351 |  | 2 | 2
|  | Information flags | 64 bits | Read only | 8A19 | 35353 | 1 | 4 | 4
|  | Reserved |  |  | 8A1D | 35357 |  | 2 | 2
|  | Warning flags | 64 bits | Read only | 8A1F | 35359 | 1 | 4 | 4
|  | Reserved |  |  | 8A23 | 35363 |  | 2 | 2
|  | Alarm flags | 64 bits (25 used now) | Read only | 8A25 | 35365 | 1 | 4 | 4
|  | Reserved |  |  | 8A29 | 35369 |  | 6 | 6
|  | Power fail counters | All, L1..L3, Any | Read only | 8A2F | 35375 | 5 | 1 | 5 |  |  | 0 | 65535 | - | - | 0 | 65535 | Unsigned
|  | Long power fail counters | All, L1..L3, Any |  | 8A34 | 35380 | 5 | 1 | 5
|  | Power outage time(s) | All, L1..L3, Any | Read only | 8A39 | 35385 | 5 | 3 | 15 | [6 empty] | 6 bytes: DDDDDD:HHMMSS |  | DateTime
|  | Reset counter (resettable active energy import) |  | Read only | 8A48 | 35400 | 1 | 4 | 4
|  | Reset counter (resettable active energy export) |  | Read only | 8A4C | 35404 | 1 | 4 | 4
|  | Reset counter (resettable reactive energy import) |  | Read only | 8A50 | 35408 | 1 | 4 | 4
|  | Reset counter (resettable reactive energy export) |  | Read only | 8A54 | 35412 | 1 | 4 | 4
|  | Reserved |  |  | 8A58 | 35416 |  | 8 | 8
|  | Timer for total use | YYMMDD:HHMMSS |  | 8A60 | 35424 | 1 | 3 | 3
|  | Timer for maintenance | YYMMDD:HHMMSS |  | 8A63 | 35427 | 1 | 3 | 3
|  | User defined identification nr |  |  | 8A66 | 35430 | 1 | 2 | 2
|  | Reserved |  |  | 8A68 | 35432 |  | 408 | 408
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 512 | 200 | 512
Settings |  | Transformer ratios | Current transf ratio | (old meters) | 8C00 | 35840 | 1 | 1 | 1 | 8C00 | 35840 | 0 | 65535 | 1 | - | 0 | 65535 | Unsigned
(Read/Write) |  |  | Voltage transf ratio | (old meters) | 8C01 | 35841 | 1 | 1 | 1 |  |  | 0 | 65535 | 1 | - | 0 | 65535 | Unsigned
|  |  | Total transf ratio | (old meters) | 8C02 | 35842 | 1 | 2 | 2 |  |  | 0 | 4294967295 | 1 | - | 0 | 4294967295 | Unsigned
|  | (Maps to same as reg 8C00) | Current transf ratio (numerator) |  | 8C04 | 35844 | 1 | 2 | 2
|  | (Maps to same as reg 8C01) | Voltage transf ratio (numerator) |  | 8C06 | 35846 | 1 | 2 | 2
|  |  | Current transf ratio (denominator) |  | 8C08 | 35848 | 1 | 2 | 2
|  |  | Voltage transf ratio (denominator) |  | 8C0A | 35850 | 1 | 2 | 2
|  | I/O settings (incl pulse outputs) | I/O signal mode | port 1 | 8C0C | 35852 | 1 | 1 | 1
|  |  | I/O signal mode | port 2 | 8C0D | 35853 | 1 | 1 | 1
|  |  | I/O signal mode | port 3 | 8C0E | 35854 | 1 | 1 | 1
|  |  | I/O signal mode | port 4 | 8C0F | 35855 | 1 | 1 | 1
|  |  | Instance nr | (1-4) | 8C10 | 35856 | 1 | 1 | 1
|  |  | I/O nr (port nr) | (1-4) | 8C11 | 35857 | 1 | 1 | 1
|  |  | Energy quantity | OBIS code | 8C12 | 35858 | 1 | 3 | 3
|  |  | Pulses / kWh |  | 8C15 | 35861 | 1 | 2 | 2
|  |  | Pulses / kvarh |  | 8C17 | 35863 | 1 | 2 | 2
|  |  | Pulse length (ms) |  | 8C19 | 35865 | 1 | 2 | 2
|  |  | Turn off pulse output |  | 8C1B | 35867 | 1 | 1 | 1
|  | Reserved |  |  | 8C1C | 35868 |  | 4 | 4
|  | Load profile settings | Channel nr | (1-8) | 8C20 | 35872 | 1 | 1 | 1
|  |  | Quantity | OBIS code | 8C21 | 35873 | 1 | 3 | 3
|  |  | Period | minutes | 8C24 | 35876 | 1 | 2 | 2
|  |  | Channel entries |  | 8C26 | 35878 | 1 | 2 | 2
|  |  | Search type | Raw=0, Smart=1 | 8C28 | 35880 | 1 | 1 | 1
|  | Reserved |  |  | 8C29 | 35881 |  | 7 | 7
|  | Demand settings | Nr of quantities - start config |  | 8C30 | 35888 | 1 | 1 | 1
|  |  | Channel nr (R only) | auto updated | 8C31 | 35889 | 1 | 1 | 1
|  |  | Channel quantity | OBIS code | 8C32 | 35890 | 1 | 3 | 3
|  |  | Level quantity | OBIS code | 8C35 | 35893 | 1 | 3 | 3
|  |  | Levels |  | 8C38 | 35896 | 1 | 1 | 1
|  |  | Interval (minutes) |  | 8C39 | 35897 | 1 | 1 | 1
|  |  | Sub interval (minutes) |  | 8C3A | 35898 | 1 | 1 | 1
|  | MSB:0=Da,1=We,2=Mo,LSB:1=mon,7=sun | Period (day/week/month + week day) |  | 8C3B | 35899 | 1 | 1 | 1
|  | Reserved |  |  | 8C3C | 35900 |  | 20 | 20
|  | Previous values settings | Nr of channels - start config |  | 8C50 | 35920 | 1 | 1 | 1
|  |  | Channel nr (R only) | auto updated | 8C51 | 35921 | 1 | 1 | 1
|  |  | Quantity | OBIS code | 8C52 | 35922 | 1 | 3 | 3
|  | MSB:0=Da,1=We,2=Mo,LSB:1=mon,7=sun | Period (day/week/month + week day) |  | 8C55 | 35925 | 1 | 1 | 1
|  | Reserved |  |  | 8C56 | 35926 |  | 10 | 10
|  | Alarm settings | Channel nr | (1-25) | 8C60 | 35936 | 1 | 1 | 1
|  |  | Quantity | OBIS | 8C61 | 35937 | 1 | 3 | 3
|  | Actions registers: | On/Off thresholds |  | 8C64 | 35940 | 1 | 8 | 8
|  | 1st reg: Actions, 2nd reg: output nr | On/Off delay | seconds | 8C6C | 35948 | 1 | 4 | 4
|  | Actions: bit0=log, bit1=output, bit2=reg. | Alarm action on/off |  | 8C70 | 35952 | 1 | 2 | 2
|  | Reserved |  |  | 8C72 | 35954 |  | 14 | 14
|  |  | Nr of channels - start config |  | 8C80 | 35968 | 1 | 1 | 1
| Not used | 1st reg: Actions, 2nd reg: output nr | Channel nr (R only) | auto updated | 8C81 | 35969 | 1 | 1 | 1
|  | Actions: bit0=log, bit1=output, bit2=reg. | Alarm action on/off |  | 8C82 | 35970 | 1 | 2 | 2
|  | Reserved |  |  | 8C84 | 35972 |  | 12 | 12
|  | Tariff settings | Source (Clock = 0, Comm = 1, Inputs = 2) |  | 8C90 | 35984 | 1 | 1 | 1
|  | high byte = amount, low byte = confbyte | Input config |  | 8C91 | 35985 | 1 | 1 | 1
|  | Calendar config | Nr of seasons - start config |  | 8C92 | 35986 | 1 | 1 | 1
|  |  | Season nr (R only) | auto updated | 8C93 | 35987 | 1 | 1 | 1
|  | name 15 reg, date 3 reg, weekpr.15 reg | Season (Name + start + weekprof.) |  | 8C94 | 35988 | 1 | 33 | 33
|  |  | Nr of week profiles - start config |  | 8CB5 | 36021 | 1 | 1 | 1
|  |  | Week prof nr (R only) | auto updated | 8CB6 | 36022 | 1 | 1 | 1
|  | name 15 reg, day ids 7 regs | Week profile (Name + 7 day IDs) |  | 8CB7 | 36023 | 1 | 22 | 22
|  |  | Nr of day profiles - start config |  | 8CCD | 36045 | 1 | 1 | 1
|  | Action ids: 0 - 3 = Activate tariff 1 - 4 | Day prof nr (R only) | auto updated | 8CCE | 36046 | 1 | 1 | 1
|  | 100 = Set output 1, 101 = Reset out 1, … | Nr of day profile actions |  | 8CCF | 36047 | 1 | 1 | 1
|  |  | Action nr (R only) | auto updated | 8CD0 | 36048 | 1 | 1 | 1
|  | hour + min 1 reg, action id 1 reg | Day profile action (time + action) |  | 8CD1 | 36049 | 1 | 2 | 2
|  |  | Nr of special days - start config |  | 8CD3 | 36051 | 1 | 1 | 1
|  |  | Spec. day nr (R only) | auto updated | 8CD4 | 36052 | 1 | 1 | 1
|  | date 2 regs, day id 1 reg | Special day entry (date + day id) |  | 8CD5 | 36053 | 1 | 3 | 3
|  | Reserved |  |  | 8CD8 | 36056 |  | 8 | 8
|  | CO2 conversion factor act energy | 0.001 - 9.999 kg / kWh |  | 8CE0 | 36064 | 1 | 2 | 2
|  | Currency conversion factor act en. | 0.001 - 999999.000 currency / kWh |  | 8CE2 | 36066 | 1 | 2 | 2
|  | LED source | 0 = Active energy, 1 = Reactive energy |  | 8CE4 | 36068 | 1 | 1 | 1
|  | Number of elements | 1-3 |  | 8CE5 | 36069 | 1 | 1 | 1
|  | DST start (month, day of month, day of week, hour) |  |  | 8CE6 | 36070 | 1 | 2 | 2
|  | DST end (month, day of month, day of week, hour) |  |  | 8CE8 | 36072 | 1 | 2 | 2
|  | DST enabled (0 = disabled, 1 = enabled) |  |  | 8CEA | 36074 | 1 | 1 | 1
|  | Reserved |  |  | 8CEB | 36075 |  | 533 | 533
Averaging times
Min/Max settings
Quantities to register in tariffs
Sub meter settings?
Time threshold for long power fail
Alarm filters
HDLC settings?
MBUS settings?
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 768 | 300 | 768
Operations |  | Reset PF counters | All, L1..L3, Any |  | 8F00 | 36608 | 5 | 1 | 5 | 8F00 | 36608 | 0 | 65535 | Write 1 to reset |  | 0 | 65535 | Unsigned
(Write only) |  | Reset outage time | All, L1..L3, Any |  | 8F05 | 36613 | 5 | 1 | 5 |  |  | 0 | 65535 | Write 1 to reset |  | 0 | 65535 | Unsigned
|  | Reset active energy (tariff 1) | Resettable energy reg (old meters) |  | 8F0A | 36618 | 1 | 1 | 1 |  |  | 0 | 65535 | Write 1 to reset |  | 0 | 65535 | Unsigned
|  | Reset input counters | 1..8 |  | 8F0B | 36619 | 8 | 1 | 8 |  |  | 0 | 65535 | Write 1 to reset |  | 0 | 65535 | Unsigned
|  | Reset stored states | 1..8 |  | 8F13 | 36627 | 8 | 1 | 8 |  |  | 0 | 65535 | Write 1 to reset |  | 0 | 65535 | Unsigned
|  | Reset active energy import | Resettable energy reg |  | 8F1B | 36635 | 1 | 1 | 1
|  | Reset active energy export | Resettable energy reg |  | 8F1C | 36636 | 1 | 1 | 1
|  | Reset reactive energy import | Resettable energy reg |  | 8F1D | 36637 | 1 | 1 | 1
|  | Reset reactive energy export | Resettable energy reg |  | 8F1E | 36638 | 1 | 1 | 1
|  | Reset Previous values | All channels |  | 8F1F | 36639 | 1 | 1 | 1
|  | Reset Demand | All channels |  | 8F20 | 36640 | 1 | 1 | 1
|  | Reset Load profile | Channel 1..8 |  | 8F21 | 36641 | 8 | 1 | 8
|  | Reserved (for 8 more load profile channels) |  |  | 8F29 | 36649 |  | 8 | 8
|  | Reset System log |  |  | 8F31 | 36657 | 1 | 1 | 1
|  | Reset Event log |  |  | 8F32 | 36658 | 1 | 1 | 1
|  | Reset Net quality log |  |  | 8F33 | 36659 | 1 | 1 | 1
|  | Reset Communication log |  |  | 8F34 | 36660 | 1 | 1 | 1
|  | Reset maintenance timer |  |  | 8F35 | 36661 | 1 | 1 | 1
|  | Reset tariff registers | Tariff quantity 1..8 | All tariff Registers | 8F36 | 36662 | 8 | 1 | 8
|  | Reserved |  |  | 8F3E | 36670 |  | 50 | 50
|  | Freeze Demand |  |  | 8F70 | 36720 | 1 | 1 | 1
|  | Send password (login) | (16 characters) |  | 8F71 | 36721 | 1 | 8 | 8
|  | Set password (modify) | (16 characters) |  | 8F79 | 36729 | 1 | 8 | 8
|  | Reserved |  |  | 8F81 | 36737 |  | 127 | 127
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 256 | 100 | 256
Minimum |  | Generic minimum channels |  |  | 9000 | 36864 |  | 43 | 43 | 9000 | 36864
(Read/Write) |  | Reserved |  |  | 902B | 36907 |  | 85 | 85
Maximum |  | Generic maximum channels |  |  | 9080 | 36992 |  | 43 | 43
|  | Reserved |  |  | 90AB | 37035 |  | 341 | 341
[9 empty] | Sum |  | Control (Dec)
Sum | [8 empty] | 512 | 200 | 512
[10 empty] | 9000 | 36864
Sub meter data?
Note on J73: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J120: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J129: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J141: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J154: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J158: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J176: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J200: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J204: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J216: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J245: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J330: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J356: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.
Note on J362: Jennifer X. Larkang: Check against the Control (Dec) two cells to the right from this cell.

## Channel data etc
Missing value handling
(What to send out to indicate that a quantity has an invalid value) |  | "Simple values" | Unsigned | FFFF in all registers
|  |  | Signed | 7FFF in most significant register, FFFF in the others
|  | Load profile |  | Set all except Channel, DateTime and Direction to FFFFFF…
|  | Billing |  | Set all except Channel, DateTime and Direction to FFFFFF…
|  | Minimum, Ch |  | Set all except Channel to FFFFFF…
|  | Minimum, Qu |  | Set all except Quantity to FFFFFF…
|  | Maximum, Ch |  | Set all except Channel to FFFFFF…
|  | Maximum, Qu |  | Set all except Quantity to FFFFFF…
|  | Tariffs |  | Set all except Channel to FFFFFF…
Selective access for Profile Generic-buffers
(How to access the data over DLMS) |  | restricting_object |  | 0, 0, 1, 0, 0, 255 (Clock)
|  | Forward | from_value | LP_DATE_TIME / DM_DATE_TIME / EV_DATE_TIME / PV_DATE_TIME
|  |  | to_value | 2099-01-01, 00:00:00 ("Infinite future")
|  | Backward | from value | LP_DATE_TIME / BILL_DATE_TIME / EV_DATE_TIME
|  |  | to_value | 2000-01-01, 00:00:00 ("Infinite past")
| Field name | Size (Registers) | (Bytes needed)
Load Profile
Control block (header) | Get next block | 1 | 1 |  | (R)W | LP_NEXT_BLOCK
| Restart | 1 | 1 | Restart reading from most recent value | (R)W | LP_RESTART
| Nr of entries | 1 | 2 |  | R | LP_NR_ENTRIES
| Channel nr | 1 | 1 |  | RW | LP_CHANNEL_NR
| DateTime | 3 | 6 | ..to start reading from (YYMMDDHHMMSS) | RW | LP_DATE_TIME
| Direction | 1 | 1 | forward/backward? | RW | LP_DIRECTION
| Capture period | 1 | 1 | storage interval (minutes) | R | LP_CAP_PERIOD
| Interval/Register values | 1 | 1 | Interval consumption/Register value
| Reserved | 6 | 0 | Reserved writeable
| Sum of Regs | 16
Data block | Quantity | 3 | 6 | OBIS code | R | LP_QUANTITY
| Scaler | 1 | 1 |  | R | LP_SCALER
| Capture period | 2 | 4 |  | R | LP_CAP_PERIOD
| Data type | 1 | 1 | DLMS data type | R | LP_DATA_TYPE
| Reserved | 9 | 0 | Reserved read only
| Timestamps + Values | 120 | 240 | Timestamp: (YYMMDDHHMMSS) | R | LP_BUFFER
| Sum of Regs | 152 |  | Values: Status (if available) + value
TS: 3 Reg, Stat: 1 Reg, Val: 4 Reg = 8
-> 15 values = 120 Regs
| Field name | Size (Registers) | (Bytes needed)
Event log
Control block | Get next block | 1 | 1 |  | W | EV_NEXT_BLOCK
| Entry number | 1 | 1 |  | RW | EV_ENTRY_NR
| Nr of entries | 1 | 2 |  | R | EV_NR_OF_ENTRIES
| Entry order | 1 | 1 |  | RW | EV_ENTRY_ORDER
| DateTime | 3 | 6 | …to start reading from | RW | EV_DATE_TIME
| Direction | 1 | 1 | backwards/forward | RW | EV_DIRECTION
| Reserved | 8 | 0
| Sum of Regs | 16
Data block | Log entries | 105 |  | 15 log entries, 7 registers each | R | EV_DATA_BLOCK
| Sum of Regs | 121
| Log entry: | Timestamp: 3 Regs, Category: 1 Reg, Event id: 1 Reg, Duration: 2 Regs
| Field name | Size (Registers) | (Bytes needed)
Demand
Control block | Get next block | 1 | 1 |  | (R)W | DM_NEXT_BLOCK
| Entry number | 1 | 1 |  | RW | DM_ENTRY_NR
| Nr of entries | 1 | 2 |  | R | DM_NR_OF_ENTRIES
| Entry order | 1 | 1 |  | RW | DM_ENTRY_ORDER
| DateTime | 3 | 6 | ..to start reading from (YYMMDDHHMMSS) | RW | DM_DATE_TIME
| Direction | 1 | 1 | forward/backward? | RW | DM_DIRECTION
| Capture period | 1 | 1 | Day/Week/Month | R | DM_CAP_PERIOD
| Interval | 1 | 1
| Sub interval | 1 | 1
| Sum of Regs | 11
Object 1 | Timestamp | 3 | 6 |  | R | DM_DATA_BLOCK
Nr of channels | Quantity channel 1 | 3 | 6 | OBIS code | R
| Level channel 1 | 1 | 1 |  | R
8 | Data type channel 1 | 1 | 1 | DLMS data type | R
(don't remove the 8 above!) | Scaler channel 1 | 1 | 1 |  | R
| Capture time channel 1 | 3 | 6
| Status channel 1 | 1 | 2 |  | R
| Value channel 1 | 4 | 8 |  | R
| Quantity channel 2 | 3 | 6 | OBIS code | R
| Level channel 2 | 1 | 1 |  | R
| Data type channel 2 | 1 | 1 | DLMS data type | R
| Scaler channel 2 | 1 | 1 |  | R
| Capture time channel 2 | 3 | 6
| Status channel 2 | 1 | 2 |  | R
| Value channel 2 | 4 | 8 |  | R
| … | 70 |  |  | R
| Quantity channel 8 | 3 | 6 | OBIS code | R
| Level channel 8 | 1 | 1 |  | R
| Data type channel 8 | 1 | 1 | DLMS data type | R
| Scaler channel 8 | 1 | 1 |  | R
| Capture time channel 2 | 3 | 6
| Status channel 8 | 1 | 2 |  | R
| Value channel 8 | 4 | 8 |  | R
| Sum of Regs | 115
Object 2..Object 7 | Same structure as object 1 |  |  | Contains data for channels 9 to 50
| Field name | Size (Registers) | (Bytes needed)
Previous values
Control block | Get next block | 1 | 1 |  | (R)W | PV_NEXT_BLOCK
| Entry number | 1 | 1 |  | RW | PV_ENTRY_NR
| Nr of entries | 1 | 2 |  | R | PV_NR_OF_ENTRIES
| Entry order | 1 | 1 |  | RW | PV_ENTRY_ORDER
| DateTime | 3 | 6 | ..to start reading from (YYMMDDHHMMSS) | RW | PV_DATE_TIME
| Direction | 1 | 1 | forward/backward? | RW | PV_DIRECTION
| Capture period | 1 | 1 | Day/Week/Month | R | PV_CAP_PERIOD
| Sum of Regs | 9
Object 1 | Timestamp | 3 | 6 |  | R | PV_DATA_BLOCK
Nr of channels | Quantity channel 1 | 3 | 6 | OBIS code | R
8 | Data type channel 1 | 1 | 1 | DLMS data type | R
(don't remove the 8 above!) | Scaler channel 1 | 1 | 1 |  | R
| Status channel 1 | 1 | 2 |  | R
| Value channel 1 | 4 | 8 |  | R
| Quantity channel 2 | 3 | 6 | OBIS code | R
| Data type channel 2 | 1 | 1 | DLMS data type | R
| Scaler channel 2 | 1 | 1 |  | R
| Status channel 2 | 1 | 2 |  | R
| Value channel 2 | 4 | 8 |  | R
| … | 50 |  |  | R
| Quantity channel 8 | 3 | 6 | OBIS code | R
| Data type channel 8 | 1 | 1 | DLMS data type | R
| Scaler channel 8 | 1 | 1 |  | R
| Status channel 8 | 1 | 2 |  | R
| Value channel 8 | 4 | 8 |  | R
| Sum of Regs | 83
Object 2..Object 7 | Same structure as object 1 |  |  | Contains data for channels 9 to 50
| Field name | Size (Registers) | (Bytes needed)
"15-min averages" | (Averages of instantaneous values, settable time, default 15 min)
Channel search | Channel | 1 | 1 |  | RW | AVG_CHANNEL_NR
| Quantity | 3 | 6 | OBIS code | R | AVG_QUANTITY
| Scaler | 1 | 1 | 0 = None or Unused | R | AVG_SCALER
| Data type | 1 | 1 |  | R | AVG_DATA_TYPE
| Value | 4 | 8 |  | R | AVG_VALUE
| Sum of Regs | 10
Quantity search | Quantity | 3 | 6 | OBIS code | RW
| Scaler | 1 | 1 |  | R
| Data type | 1 | 1 |  | R
| Value | 4 | 8 |  | R
| Sum of Regs | 9
| Field name | Size (Registers) | (Bytes needed)
Minimum
Channel search | Channel | 1 | 1 |  | RW | MIN_CHANNEL_NR
| Quantity | 3 | 6 | OBIS code | R | MIN_QUANTITY
| Scaler | 1 | 1 |  | R | MIN_SCALER
| Averaging time | 1 | 2 | Seconds/Averaging period number | R | MIN_AVG_TIME
| Numer of periods | 1 | 1 | If we want to allow sliding window | R | MIN_PERIODS
| Data type | 1 | 1 |  | R | MIN_DATA_TYPE
| DateTime | 3 | 6 | (Year low, Month, Day, Hour, Min, Sec) | R | MIN_DATE_TIME1
| Value | 4 | 8 |  | R | MIN_VALUE1
| DateTime | 3 | 6 |  | R | MIN_DATE_TIME2
| Value | 4 | 8 |  | R | MIN_VALUE2
| DateTime | 3 | 6 |  | R | MIN_DATE_TIME3
| Value | 4 | 8 |  | R | MIN_VALUE3
| DateTime | 3 | 6 |  | R | MIN_DATE_TIME4
| Value | 4 | 8 |  | R | MIN_VALUE4
| DateTime | 3 | 6 |  | R | MIN_DATE_TIME5
| Value | 4 | 8 |  | R | MIN_VALUE5
| Sum of Regs | 43
Quantity search | Quantity | 3 | 6 | OBIS code | RW
| DateTime | 3 | 6 | (Year low, Month, Day, Hour, Min, Sec) | R
| Scaler | 1 | 1 |  | R
| Averaging time | 1 | 2 | Seconds | R
| Numer of periods | 1 | 1 | If we want to allow sliding window | R
| Data type | 1 | 1 |  | R
| Value | 4 | 8 |  | R
| Sum of Regs | 14
| Field name | Size (Registers) | (Bytes needed)
Maximum
Channel search | Channel | 1 | 1 |  | RW | MAX_CHANNEL_NR
| Quantity | 3 | 6 | OBIS? | R | MAX_QUANTITY
| Scaler | 1 | 1 |  | R | MAX_SCALER
| Averaging time | 1 | 2 | Seconds/Averaging period number | R | MAX_AVG_TIME
| Numer of periods | 1 | 1 | If we want to allow sliding window | R | MAX_PERIODS
| Data type | 1 | 1 |  | R | MAX_DATA_TYPE
| DateTime | 3 | 6 | (Year low, Month, Day, Hour, Min, Sec) | R | MAX_DATE_TIME1
| Value | 4 | 8 |  | R | MAX_VALUE1
| DateTime | 3 | 6 |  | R | MAX_DATE_TIME2
| Value | 4 | 8 |  | R | MAX_VALUE2
| DateTime | 3 | 6 |  | R | MAX_DATE_TIME3
| Value | 4 | 8 |  | R | MAX_VALUE3
| DateTime | 3 | 6 |  | R | MAX_DATE_TIME4
| Value | 4 | 8 |  | R | MAX_VALUE4
| DateTime | 3 | 6 |  | R | MAX_DATE_TIME5
| Value | 4 | 8 |  | R | MAX_VALUE5
| Sum of Regs | 43
Quantity search | Quantity | 3 | 6 | OBIS code | RW
| DateTime | 3 | 6 | (Year low, Month, Day, Hour, Min, Sec) | R
| Scaler | 1 | 1 |  | R
| Averaging time | 1 | 2 | Seconds | R
| Numer of periods | 1 | 1 | If we want to allow sliding window | R
| Data type | 1 | 1 |  | R
| Value | 4 | 8 |  | R
| Sum of Regs | 14
| Field name | Size (Registers) | (Bytes needed)
Tariffs
| Channel | 1 | 1 | Channel 1 = fixed to Active energy imp | RW | TF_CHANNEL_NR
| Quantity | 3 | 6 | Channel 2 = fixed to Reactive energy imp | R | TF_QUANTITY
| Scaler | 1 | 1 | Channel 1 and 2 are mapped to other | R | TF_SCALER
| Data type | 1 | 1 | Registers as well | R | TF_DATA_TYPE
| Value (16 tariffs) | 64 | 128 | (8 bytes * 16 tariffs) | R | TF_VALUES
| Sum of Regs | 70

## ModCom map Auto
Quantity | Get (code 3) | Set (code 16) |  | Details 1 | Details 2 | Register(s) | Reg (Dec) | Number of quantities | Size | Nr of registers
Active imp | X |  | Active imp | kWh |  | 5000 | 20480 | 1 | 4 | 4
Active exp | X |  | Active exp | kWh |  | 5004 | 20484 | 1 | 4 | 4
Reactive imp | X |  | Reactive imp | kvarh |  | 500C | 20492 | 1 | 4 | 4
Reactive exp | X |  | Reactive exp | kvarh |  | 5010 | 20496 | 1 | 4 | 4
Active imp (tariffs) | X |  | Active imp | kWh | Tariff 1..4 | 5170 | 20848 | 4 | 4 | 16
Reactive imp (tariffs) | X |  | Reactive imp | kvarh | Tariff 1..4 | 51B0 | 20912 | 4 | 4 | 16
Voltages | X |  | Voltages | L1..L3 |  | 5B00 | 23296 | 3 | 2 | 6
| X |  |  | L1-L2 |  | 5B06 | 23302 | 1 | 2 | 2
| X |  |  | L3-L2 |  | 5B08 | 23304 | 1 | 2 | 2
Currents | X |  | Currents | L1..L3 |  | 5B0C | 23308 | 3 | 2 | 6
Powers (imp-exp) | X |  | Powers | Active | Total, L1..L3 | 5B14 | 23316 | 4 | 2 | 8
| X |  |  | Reactive | Total, L1..L3 | 5B1C | 23324 | 4 | 2 | 8
| X |  |  | Apparent | Total, L1..L3 | 5B24 | 23332 | 4 | 2 | 8
Frequency | X |  | Frequency |  |  | 5B2C | 23340 | 1 | 1 | 1
Phase angles | X |  | Phase angles | Power | Total, L1..L3 | 5B2D | 23341 | 4 | 1 | 4
| X |  |  | Voltage | L1..L3 | 5B31 | 23345 | 3 | 1 | 3
| X |  |  | Current | L1..L3 | 5B37 | 23351 | 3 | 1 | 3
Power factors | X |  | Power factors |  | Total, L1..L3 | 5B3A | 23354 | 4 | 1 | 4
Current quadrant | X |  | Current quadrant |  | Total, L1..L3 | 5B3E | 23358 | 4 | 1 | 4
Inputs | X |  | Outputs | Input 1..2 | (1 Reg each) | 6300 | 25344 | 8 | 1 | 8
Outputs | X | X | Inputs | Output 1..2 | (1 Reg each) | 6308 | 25352 | 8 | 1 | 8
Stored inputs | X |  | Stored inputs | Input 1..2 | (1 Reg each) | 6310 | 25360 | 8 | 1 | 8
Counters | X |  | Counters | Input 1..2 |  | 6318 | 25368 | 2 | 4 | 8
Serial number | X |  | Serial number(s) |  |  | 8900 | 35072 | 1 | 2 | 2
Firmware version | X |  | Meter firmware version |  |  | 8908 | 35080 | 1 | 8 | 8
Date Time | X | X | Date Time | YYMMDD:HHMMSS |  | 8A00 | 35328 | 1 | 3 | 3
Day of week | X |  | Day of week |  |  | 8A03 | 35331 | 1 | 1 | 1
DST | X |  | DST active |  |  | 8A04 | 35332 | 1 | 1 | 1
Day type | X |  | Active day type |  |  | 8A05 | 35333 | 1 | 1 | 1
Season | X |  | Active season |  |  | 8A06 | 35334 | 1 | 1 | 1
Current tariff | X |  | Current tariff (1-4) | 1 instance! |  | 8A07 | 35335 | 1 | 1 | 1
Error flags | X |  | Error flags (old meters) | 64 bit |  | 8A0F | 35343 | 1 | 4 | 4
Power fail counter | X |  | Power fail counters | All phases |  | 8A2F | 35375 | 1 | 1 | 1
Power outage time | X |  | Power outage time(s) | All phases |  | 8A39 | 35385 | 1 | 3 | 3
Reset power fail counter |  | X | Reset PF counters | All phases |  | 8F00 | 36608 | 1 | 1 | 1
Reset outage time |  | X | Reset outage time | All phases |  | 8F05 | 36613 | 1 | 1 | 1
Reset energy |  | X | Reset active energy (tariff 1) | Resettable energy reg (old meters) |  | 8F0A | 36618 | 1 | 1 | 1
Reset input counters |  | X | Reset input counters | Input 1..2 |  | 8F0B | 36619 | 2 | 1 | 2
Reset stored states |  | X | Reset stored states | Input 1..2 |  | 8F13 | 36627 | 2 | 1 | 2
Transformer ratios | X |  | Transformer ratios | Current transf ratio |  | 8C00 | 35840 | 1 | 1 | 1
| X |  |  | Voltage transf ratio |  | 8C01 | 35841 | 1 | 1 | 1
| X |  |  | Total transf ratio |  | 8C02 | 35842 | 1 | 2 | 2
Blue = Manually typed for ModCom!!

## Sace analyzer
Identity | Meter Quantity | (bytes) |  |  | Modbus | Modbus | (bytes) |  |  | DLMS
|  | Cewe Size | Datatyp | Enhet | Cewe reg | SACE | Size | Datatyp | Enhet | A | B | C | D | E | F | Description | Interface class | Allowed data types | Chosen data type | Unit | Scaler | Primitive | Attribute
Read-001 | Meter Serial Number |  |  |  | >4000 | 1A00 | 14 (10!) | String | - | 0 | 0 | 96 | 1 | 0 | 255 | Device ID (manufacturing number) | Data/Profile gen/Reg table | OCT-str |  | 255 | 0 | Get | value
Read-002 | Active Imported Energy, Total |  |  |  |  | 107C | 8 | Unsign. | milli | 1 | 0 | 1 | 8 | 0 | 255 | ∑Li Active power+ (QI+QIV) Time integral 1 | Reg / Ext reg | "Choice" |  |  | -3 | Get | value
- " - | - " - | - " - | - " - | - " - |  | 2A50 | 8 | U. double | kilo/mega | 1 | 0 | 1 | 8 | 0 | 255 | - " - | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-003 | Active Imported Energy, Tariff 1 |  |  |  |  | 2A60 | 8 | U. double | kilo/mega | 1 | 0 | 1 | 8 | 1 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-004 | Active Imported Energy, Tariff 2 |  |  |  |  | 2A70 | 8 | U. double | kilo/mega | 1 | 0 | 1 | 8 | 2 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-005 | Active Imported Energy, Tariff 3 |  |  |  |  | 2A80 | 8 | U. double | kilo/mega | 1 | 0 | 1 | 8 | 3 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-006 | Active Imported Energy, Tariff 4 |  |  |  |  | 2A90 | 8 | U. double | kilo/mega | 1 | 0 | 1 | 8 | 4 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-007 | Reactive Imported Energy, Total |  |  |  |  | 1080 | 8 | Unsign. | milli | 1 | 0 | 3 | 8 | 0 | 255 | ∑Li Reactive power+ (QI+QII) Time integral 1 | Reg / Ext reg | "Choice" |  |  | -3 | Get | value
- " - | - " - | - " - | - " - | - " - |  | 2A58 | 8 | U. double | kilo/mega | 1 | 0 | 3 | 8 | 0 | 255 | - " - | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-008 | Reactive Imported Energy, Tariff 1 |  |  |  |  | - | - (8) | - | - | 1 | 0 | 3 | 8 | 1 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-009 | Reactive Imported Energy, Tariff 2 |  |  |  |  | - | - (8) | - | - | 1 | 0 | 3 | 8 | 2 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-010 | Reactive Imported Energy, Tariff 3 |  |  |  |  | - | - (8) | - | - | 1 | 0 | 3 | 8 | 3 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-011 | Reactive Imported Energy, Tariff 4 |  |  |  |  | - | - (8) | - | - | 1 | 0 | 3 | 8 | 4 | 255 | -"- | Reg / Ext reg | "Choice" |  |  | 3/6 | Get | value
Read-012 | Current Tariff |  |  |  |  | Make space for 16… |  |  |  | 0 | 0 | 96 | 14 | 0 | 255 | Currently active tariff (#1) | Data/Reg/Ext reg |  |  |  |  | Get | value
Read-013 | Transformer Ratio |  |  |  |  | - |  | - | - | 1 | 0 | 0 | 4 | 4 | 255 | Overall transformer ratio (numerator) | Fråga Ulf! |  |  |  |  | Get
Read-014 | Current Transformer Ratio |  |  |  |  | 1A2B | 2 | Unsign. | - | 1 | 0 | 0 | 4 | 2 | 255 | Transformer ratio - current (numerator) | Data/Reg/Ext reg | "Simple data type" |  |  |  | Get | value
Read-015 | Voltage Transformer Ratio |  |  |  |  | 1A2C | 2 | Unsign. | - | 1 | 0 | 0 | 4 | 3 | 255 | Transformer ratio - voltage (numerator) | Data/Reg/Ext reg | "Simple data type" |  |  |  | Get | value
Read-016 | Time (and Date) |  |  |  |  | 1A21 | 6 | Oct str. | HHMMSS | 0 | 0 | 1 | 0 | 0 | 255 | Clock: attr time | Clock | OCT-str (date_time) |  |  |  | Get | time (time-part)
Read-0XX | Date |  |  |  |  | 1A25 | 6 | Oct str. | YYMMDD | 0 | 0 | 1 | 0 | 0 | 255 | Clock: attr time | Clock | OCT-str (date_time) |  |  |  | Get | time (date-part)
Read-017 | DST Status |  |  |  |  | - |  | - | - | 0 | 0 | 1 | 0 | 0 | 255 | Clock attr: daylight_savings_enabled | Clock | Boolean |  |  |  | Get | daylight_savings_enabled
Read-018 | 64 bit Error Flag |  |  |  |  | - |  | - | - | 0 | 0 | 97 | 97 | 0 | 255 | General error object | Data/Profile gen/Reg table | OCT-str/Bit-str | Bit-str | 255 | 0 | Get | value
Read-019 | Power Fail Counter |  |  |  |  | - |  | - | - | 0 | 0 | 96 | 7 | 0 | 255 | Power failure events (in all three phases) | Data/Reg/Ext reg | U / LU / DLU / L64U |  | 255? | 0? | Get | value
Read-020 | Power Outage Time |  |  |  |  | - |  | - | - | 0 | 0 | 96 | 7 | 10 | 255 | Time of power failure (in all three phases) | Data/Reg/Ext reg | time / date_time ?? |  | second | 0 | Get | value
Read-021 | Meter Firmware Version |  |  |  |  | 1A05 | 10 (14!) | String | None | 1 | 0 | 0 | 2 | 0 | 255 | Active firmware identifier | Data/Reg/Ext reg | U/LU/OCT-str |  | 255 | 0 | Get | value
Read-022 | Active Exported Energy, Total |  |  |  |  | 2A54 | 8 | U. double | kilo/mega | 1 | 0 | 2 | 8 | 0 | 255 | ∑Li Active power- (QII+QIII) Time integral 1 | Reg / Ext reg | "Choice" |  |  |  | Get | value
Read-023 | Reactive Exported Energy, Total |  |  |  |  | 2A5C | 8 | U. double | kilo/mega | 1 | 0 | 4 | 8 | 0 | 255 | ∑Li Reactive power- (QIII+QIV) Time integral 1 | Reg / Ext reg | "Choice" |  |  |  | Get | value
Read-024 | Active Power, Total |  |  |  |  | 105C | 8 | Signed | milli | 1 | 0 | 16 | 7 | 0 | 255 | ∑Li Active power (abs(QI+QIV) - abs(QII+QIII)), Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-025 | Active Power, L1 |  |  |  |  | 1060 | 8 | Signed | milli | 1 | 0 | 36 | 7 | 0 | 255 | L1 Active power (abs(QI+QIV) - abs(QII+QIII)), Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-026 | Active Power, L2 |  |  |  |  | 1064 | 8 | Signed | milli | 1 | 0 | 56 | 7 | 0 | 255 | L2 Active power (abs(QI+QIV) - abs(QII+QIII)), Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-027 | Active Power, L3 |  |  |  |  | 1068 | 8 | Signed | milli | 1 | 0 | 76 | 7 | 0 | 255 | L3 Active power (abs(QI+QIV) - abs(QII+QIII)), Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-028 | Reactive Power, Total |  |  |  |  | 106C | 8 | Signed | milli | 1 | 0 | 3 | 7 | 0 | 255 | ∑Li Reactive power+ (QI+QIV) Instant. value (Check: Can we use pos value, as for App. Pow?) | Reg | "Choice" |  |  |  | Get | value
Read-029 | Reactive Power, L1 |  |  |  |  | 1070 | 8 | Signed | milli | 1 | 0 | 23 | 7 | 0 | 255 | ∑L1 Reactive power+ (QI+QIV) Instant. value (Check: Can we use pos value, as for App. Pow?) | Reg | "Choice" |  |  |  | Get | value
Read-030 | Reactive Power, L2 |  |  |  |  | 1074 | 8 | Signed | milli | 1 | 0 | 43 | 7 | 0 | 255 | ∑L2 Reactive power+ (QI+QIV) Instant. value (Check: Can we use pos value, as for App. Pow?) | Reg | "Choice" |  |  |  | Get | value
Read-031 | Reactive Power, L3 |  |  |  |  | 1078 | 8 | Signed | milli | 1 | 0 | 63 | 7 | 0 | 255 | ∑L3 Reactive power+ (QI+QIV) Instant. value (Check: Can we use pos value, as for App. Pow?) | Reg | "Choice" |  |  |  | Get | value
Read-032 | Apparent Power, Total |  |  |  |  | 104C | 8 | Signed | milli | 1 | 0 | 9 | 7 | 0 | 255 | ∑Li Apparent power+ (QI+QIV) Instant. value | Reg | "Choice" |  |  |  | Get | value
Read-033 | Apparent Power, L1 |  |  |  |  | 1050 | 8 | Signed | milli | 1 | 0 | 29 | 7 | 0 | 255 | L1 Apparent power+ (QI+QIV) Instant. value | Reg | "Choice" |  |  |  | Get | value
Read-034 | Apparent Power, L2 |  |  |  |  | 1054 | 8 | Signed | milli | 1 | 0 | 49 | 7 | 0 | 255 | L2 Apparent power+ (QI+QIV) Instant. value | Reg | "Choice" |  |  |  | Get | value
Read-035 | Apparent Power, L3 |  |  |  |  | 1058 | 8 | Signed | milli | 1 | 0 | 69 | 7 | 0 | 255 | L3 Apparent power+ (QI+QIV) Instant. value | Reg | "Choice" |  |  |  | Get | value
Read-036 | Voltage L1 – N |  |  |  |  | 1004 | 8 | Unsign. | milli | 1 | 0 | 32 | 7 | 0 | 255 | L1 Voltage - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-037 | Voltage L2 – N |  |  |  |  | 1008 | 8 | Unsign. | milli | 1 | 0 | 52 | 7 | 0 | 255 | L2 Voltage - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-038 | Voltage L3 – N |  |  |  |  | 100C | 8 | Unsign. | milli | 1 | 0 | 72 | 7 | 0 | 255 | L3 Voltage - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-039 | Voltage L1 – L2 |  |  |  |  | 1010 | 8 | Unsign. | milli | 1 | 0 | 32 | 7 | 0 | 255 | L1 Voltage - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-040 | Voltage L3 – L2 |  |  |  |  | 1014 | 8 | Unsign. | milli | 1 | 0 | 72 | 7 | 0 | 255 | L3 Voltage - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-041 | Current L1 |  |  |  |  | 1020 | 8 | Signed | milli | 1 | 0 | 31 | 7 | 0 | 255 | L1 Current - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-042 | Current L2 |  |  |  |  | 1024 | 8 | Signed | milli | 1 | 0 | 51 | 7 | 0 | 255 | L2 Current - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-043 | Current L3 |  |  |  |  | 1028 | 8 | Signed | milli | 1 | 0 | 71 | 7 | 0 | 255 | L3 Current - Instantaneous value | Reg | "Choice" |  |  |  | Get | value
Read-044 | Frequency |  |  |  |  | 108C | 8 | Unsign. | milli | 1 | 0 | 14 | 7 | 0 | 255 | Supply frequency | Reg | "Choice" |  |  |  | Get | value
Read-045 | Power Factor, Total | 2 |  |  |  | 102C | 8 | Signed | - (check!) | 1 | 0 | 13 | 7 | 0 | 255 | ∑Li Power factor- (active power+/apparent power+) = 0 when exporting energy?? | Reg | "Choice" |  |  |  | Get | value
Read-046 | Power Factor, L1 | 2 |  |  |  | 1030 | 8 | Signed | - (check!) | 1 | 0 | 33 | 7 | 0 | 255 | L1 Power factor = 0 when exporting energy?? | Reg | "Choice" |  |  |  | Get | value
Read-047 | Power Factor, L2 | 2 |  |  |  | 1034 | 8 | Signed | - (check!) | 1 | 0 | 53 | 7 | 0 | 255 | L2 Power factor = 0 when exporting energy?? | Reg | "Choice" |  |  |  | Get | value
Read-048 | Power Factor, L3 | 2 |  |  |  | 1038 | 8 | Signed | - (check!) | 1 | 0 | 73 | 7 | 0 | 255 | L3 Power factor = 0 when exporting energy?? | Reg | "Choice" |  |  |  | Get | value
Read-049 | Phase Angle Power, Total |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific (?) | [5 empty] | Get
Read-050 | Phase Angle Power, L1 |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific (?) | [5 empty] | Get
Read-051 | Phase Angle Power, L2 |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific (?) | [5 empty] | Get
Read-052 | Phase Angle Power, L3 |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific (?) | [5 empty] | Get
Read-053 | Phase Angle Voltage, L1 |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 0 | 255 | Phase angle From U(L1) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-054 | Phase Angle Voltage, L2 |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 1 | 255 | Phase angle From U(L2) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-055 | Phase Angle Voltage, L3 |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 2 | 255 | Phase angle From U(L3) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-0XX | Phase Angle Voltage, L1-L2 (Other log.dev.) |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 0 | 255 | Phase angle From U(L1) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-0XX | Phase Angle Voltage, L3-L2 (Other log.dev.) |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 2 | 255 | Phase angle From U(L3) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-056 | Phase Angle Current, L1 |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 4 | 255 | Phase angle From I(L1) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-057 | Phase Angle Current, L2 |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 5 | 255 | Phase angle From I(L2) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-058 | Phase Angle Current, L3 |  |  |  |  | - |  | - |  | 1 | 0 | 81 | 7 | 6 | 255 | Phase angle From I(L3) To (reference) U(L1) | Reg | "Choice" |  |  |  | Get | value
Read-059 | Current Quadrant, Total |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific | [5 empty] | Get
Read-060 | Current Quadrant, L1 |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific | [5 empty] | Get
Read-061 | Current Quadrant, L2 |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific | [5 empty] | Get
Read-062 | Current Quadrant, L3 |  |  |  |  | - |  | - | [7 empty] | Manufacturer specific | [5 empty] | Get
Read-063 | Input 1, Current State |  |  |  |  | ? |  | ? |  | 0 | 0 | 96 | 3 | 1 | 255 | State of input control signals (bit0 = input 1) | Reg |  |  |  |  | Get | value (bit0)
Read-064 | Input 2, Current State |  |  |  |  | ? |  | ? |  | 0 | 0 | 96 | 3 | 1 | 255 | State of input control signals (bit1 = input 2) | Reg |  |  |  |  | Get | value (bit1)
Read-065 | Input 1, Stored State |  |  |  |  | - |  | - | [13 empty] | Get
Read-066 | Input 2, Stored State |  |  |  |  | - |  | - | [13 empty] | Get
Read-067 | Counter 1 (Input 1) |  |  |  |  | ? |  | ? |  | 1 | 0 | 82 | 8 | 0 | 255 | Unitless quantities (pulses or pieces) Time integr. 1 | Reg | "Choice" |  |  |  | Get | value
Read-068 | Counter 2 (Input 2) |  |  |  |  | ? |  | ? |  | 1 | 0 | 82 | 8 | 1 | 255 | Unitless quantities (pulses or pieces) Time integr. 1 | Reg | "Choice" |  |  |  | Get | value
Read-069 | Output 1, Current State |  |  |  |  | ? |  | ? |  | 0 | 0 | 96 | 3 | 2 | 255 | State of output control signals (bit0 = input 1) | Reg |  |  |  |  | Get | value (bit0)
Read-070 | Output 2, Current State |  |  |  |  | ? |  | ? |  | 0 | 0 | 96 | 3 | 2 | 255 | State of output control signals (bit1 = input 2) | Reg |  |  |  |  | Get | value (bit1)
Read-071 | Previous Values (Daily and Monthly Values) |  |  |  |  | ? |  | ? |  | 1 | 0 | 98 | 1 | 0..M | 255 | Data of billing period 1, M = max nr of channels, 1 quantity (plus timestamps) per channel | Profile generic/"Simple object" |  |  |  |  | Get | buffer
Noteringar:
Blue = added for Modbus com module (ModCom)
There is info in the M-Bus telegrams if it is a 2 or 3
element meter
unsigned = U
long-unsigned = LU
double-long-unsigned = DLU
long64-unsigned = L64U
Octet string = OCT-str
Bit string = Bit-str