## Mapping Table
Parameter | Unit | Details | Resolution | EQ Meter Difference | Functionality | Data Type | Access | Register (Hex) | Reg (Dec) | Nr of quantities | Size [Byte] | Nr of registers
Active Import Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5000 | 20480 | 1 | 4 | 4
Active Export Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5004 | 20484 | 1 | 4 | 4
Active Net Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5008 | 20488 | 1 | 4 | 4
Reactive Import Energy Total | kVarh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 500C | 20492 | 1 | 4 | 4
Reactive Export Energy Total | kVarh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5010 | 20496 | 1 | 4 | 4
Reactive Net Energy Total | kVarh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5014 | 20500 | 1 | 4 | 4
Apparent Energy Total | kVAh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5018 | 20504 | 1 | 4 | 4
Reserved | [8 empty] | 20508 | 8 | 1 | 8
Equivalent CO2 on Active Imp. Energy Tot. | g/KWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5024 | 20516 | 1 | 4 | 4
Reserved | [8 empty] | 20520 | 12 | 1 | 12
Equivalent Currency on Active Imp. Energy Tot. | Currency/KWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5034 | 20532 | 1 | 4 | 4
Equivalent Currency on Active Exp. Energy Tot. | Currency/KWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5038 | 20536 | 1 | 4 | 4
Reserved | [7 empty] | 503C | 20540 | 308 | 1 | 308
Active Import Energy Total Tariff | kWh | Tariff 1..4 | 0.1 |  | Metering/Energy | Unsigned | Read | 5170 | 20848 | 4 | 4 | 16
Reserved | [7 empty] | 5180 | 20864 | 4 | 4 | 16
Active Export Energy Total Tariff | kWh | Tariff 1..4 | 0.1 |  | Metering/Energy | Unsigned | Read | 5190 | 20880 | 4 | 4 | 16
Reserved | [7 empty] | 51A0 | 20896 | 16 | 1 | 16
Rective Import Energy Total Tariff | kVarh | Tariff 1..4 | 0.1 |  | Metering/Energy | Unsigned | Read | 51B0 | 20912 | 4 | 4 | 16
Reserved | [7 empty] | 51C0 | 20928 | 16 | 1 | 16
Rective Export Energy Total Tariff | kVarh | Tariff 1..4 | 0.1 |  | Metering/Energy | Unsigned | Read | 51D0 | 20944 | 4 | 4 | 16
Reserved | [7 empty] | 51E0 | 20960 | 16 | 1 | 16
Apparent Energy Total Tariff | kVAh | Tariff 1..4 | 0.1 |  | Metering/Energy | Unsigned | Read | 51F0 | 20976 | 4 | 4 | 16
Reserved | [7 empty] | 5200 | 20992 | 608 | 1 | 608
Active Import Energy L1 | kWh | L1 | 0.1 |  | Metering/Energy | Unsigned | Read | 5460 | 21600 | 1 | 4 | 4
Active Import Energy L2 | kWh | L2 | 0.1 |  | Metering/Energy | Unsigned | Read | 5464 | 21604 | 1 | 4 | 4
Active Import Energy L3 | kWh | L3 | 0.1 |  | Metering/Energy | Unsigned | Read | 5468 | 21608 | 1 | 4 | 4
Active Export Energy L1 | kWh | L1 | 0.1 |  | Metering/Energy | Unsigned | Read | 546C | 21612 | 1 | 4 | 4
Active Export Energy L2 | kWh | L2 | 0.1 |  | Metering/Energy | Unsigned | Read | 5470 | 21616 | 1 | 4 | 4
Active Export Energy L3 | kWh | L3 | 0.1 |  | Metering/Energy | Unsigned | Read | 5474 | 21620 | 1 | 4 | 4
Reserved | [7 empty] | 5478 | 21624 | 12 | 1 | 12
Reactive Import Energy L1 | kVArh | L1 | 0.1 |  | Metering/Energy | Unsigned | Read | 5484 | 21636 | 1 | 4 | 4
Reactive Import Energy L2 | kVArh | L2 | 0.1 |  | Metering/Energy | Unsigned | Read | 5488 | 21640 | 1 | 4 | 4
Reactive Import Energy L3 | kVArh | L3 | 0.1 |  | Metering/Energy | Unsigned | Read | 548C | 21644 | 1 | 4 | 4
Reactive Export Energy L1 | kVArh | L1 | 0.1 |  | Metering/Energy | Unsigned | Read | 5490 | 21648 | 1 | 4 | 4
Reactive Export Energy L2 | kVArh | L2 | 0.1 |  | Metering/Energy | Unsigned | Read | 5494 | 21652 | 1 | 4 | 4
Reactive Export Energy L3 | kVArh | L3 | 0.1 |  | Metering/Energy | Unsigned | Read | 5498 | 21656 | 1 | 4 | 4
Reserved | [7 empty] | 549C | 21660 | 12 | 1 | 12
Apparent Energy L1 | kVAh | L1 | 0.1 |  | Metering/Energy | Unsigned | Read | 54A8 | 21672 | 1 | 4 | 4
Apparent Energy L2 | kVAh | L2 | 0.1 |  | Metering/Energy | Unsigned | Read | 54AC | 21676 | 1 | 4 | 4
Apparent Energy L3 | kVAh | L3 | 0.1 |  | Metering/Energy | Unsigned | Read | 54B0 | 21680 | 1 | 4 | 4
Reserved | [7 empty] | 54B4 | 21684 | 120 | 1 | 120
Partial Active Import Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 552C | 21804 | 1 | 4 | 4
Partial Active Export Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5530 | 21808 | 1 | 4 | 4
Partial Reactive Import Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5534 | 21812 | 1 | 4 | 4
Partial Reactive Export Energy Total | kWh |  | 0.1 |  | Metering/Energy | Unsigned | Read | 5538 | 21816 | 1 | 4 | 4
Reserved | [7 empty] | 553C | 21820 | 1476 | 1 | 1476
Voltage L1-N | V | L1 | 0.1 |  | Metering/Instant | Unsigned | Read | 5B00 | 23296 | 1 | 2 | 2
Voltage L2-N | V | L2 | 0.1 |  | Metering/Instant | Unsigned | Read | 5B02 | 23298 | 1 | 2 | 2
Voltage L3-N | V | L3 | 0.1 |  | Metering/Instant | Unsigned | Read | 5B04 | 23300 | 1 | 2 | 2
Voltage L1-L2 | V | L1-L2 | 0.1 |  | Metering/Instant | Unsigned | Read | 5B06 | 23302 | 1 | 2 | 2
Voltage L2-L3 | V | L2-L3 | 0.1 |  | Metering/Instant | Unsigned | Read | 5B08 | 23304 | 1 | 2 | 2
Voltage L3-L1 | V | L3-L1 | 0.1 |  | Metering/Instant | Unsigned | Read | 5B0A | 23306 | 1 | 2 | 2
Current L1 | A | L1 | 0.01 |  | Metering/Instant | Unsigned | Read | 5B0C | 23308 | 1 | 2 | 2
Current L2 | A | L2 | 0.01 |  | Metering/Instant | Unsigned | Read | 5B0E | 23310 | 1 | 2 | 2
Current L3 | A | L3 | 0.01 |  | Metering/Instant | Unsigned | Read | 5B10 | 23312 | 1 | 2 | 2
Current IN | A | Neutral | 0.01 |  | Metering/Instant | Unsigned | Read | 5B12 | 23314 | 1 | 2 | 2
Active Power Total | W | Total | 0.01 |  | Metering/Instant | Signed | Read | 5B14 | 23316 | 1 | 2 | 2
Active Power L1 | W | L1 | 0.01 |  | Metering/Instant | Signed | Read | 5B16 | 23318 | 1 | 2 | 2
Active Power L2 | W | L2 | 0.01 |  | Metering/Instant | Signed | Read | 5B18 | 23320 | 1 | 2 | 2
Active Power L3 | W | L3 | 0.01 |  | Metering/Instant | Signed | Read | 5B1A | 23322 | 1 | 2 | 2
Reactive Power Total | Var | Total | 0.01 |  | Metering/Instant | Signed | Read | 5B1C | 23324 | 1 | 2 | 2
Reactive Power L1 | Var | L1 | 0.01 |  | Metering/Instant | Signed | Read | 5B1E | 23326 | 1 | 2 | 2
Reactive Power L2 | Var | L2 | 0.01 |  | Metering/Instant | Signed | Read | 5B20 | 23328 | 1 | 2 | 2
Reactive Power L3 | Var | L3 | 0.01 |  | Metering/Instant | Signed | Read | 5B22 | 23330 | 1 | 2 | 2
Apparent Power Total | VA | Total | 0.01 |  | Metering/Instant | Signed | Read | 5B24 | 23332 | 1 | 2 | 2
Apparent Power L1 | VA | L1 | 0.01 |  | Metering/Instant | Signed | Read | 5B26 | 23334 | 1 | 2 | 2
Apparent Power L2 | VA | L2 | 0.01 |  | Metering/Instant | Signed | Read | 5B28 | 23336 | 1 | 2 | 2
Apparent Power L3 | VA | L3 | 0.01 |  | Metering/Instant | Signed | Read | 5B2A | 23338 | 1 | 2 | 2
Frequency | Hz |  | 0.1 |  | Metering/Instant | Signed | Read | 5B2C | 23340 | 1 | 1 | 1
Reserved | [7 empty] | 5B2D | 23341 | 13 | 1 | 13
Power Factor Total | No Unit | Total | 0.001 |  | Metering/Instant | Signed | Read | 5B3A | 23354 | 1 | 1 | 1
Power Factor L1 | No Unit | L1 | 0.001 |  | Metering/Instant | Signed | Read | 5B3B | 23355 | 1 | 1 | 1
Power Factor L2 | No Unit | L2 | 0.001 |  | Metering/Instant | Signed | Read | 5B3C | 23356 | 1 | 1 | 1
Power Factor L3 | No Unit | L3 | 0.001 |  | Metering/Instant | Signed | Read | 5B3D | 23357 | 1 | 1 | 1
Quadrant Total | No Unit | Total | 0.001 |  | Metering/Instant | Unsigned | Read | 5B3E | 23358 | 1 | 1 | 1
Quadrant L1 | No Unit | L1 | 0.001 |  | Metering/Instant | Unsigned | Read | 5B3F | 23359 | 1 | 1 | 1
Quadrant L2 | No Unit | L2 | 0.001 |  | Metering/Instant | Unsigned | Read | 5B40 | 23360 | 1 | 1 | 1
Quadrant L3 | No Unit | L3 | 0.001 |  | Metering/Instant | Unsigned | Read | 5B41 | 23361 | 1 | 1 | 1
Reserved | [7 empty] | 5B42 | 23362 | 6 | 1 | 6
Cosine Phi L1 | No Unit | L1 | 0.001 |  | Metering/Instant | Signed | Read | 5B48 | 23368 | 1 | 1 | 1
Cosine Phi L2 | No Unit | L2 | 0.001 |  | Metering/Instant | Signed | Read | 5B49 | 23369 | 1 | 1 | 1
Cosine Phi L3 | No Unit | L3 | 0.001 |  | Metering/Instant | Signed | Read | 5B4A | 23370 | 1 | 1 | 1
Reserved | [7 empty] | 5B4B | 23371 | 1973 | 1 | 1973
Communication Status Register | No Unit |  |  |  | I/O |  | Read/Write | 6300 | 25344 | 1 | 1 | 1
Reserved | [6 empty] | Read | 6301 | 25345 | 7 | 1 | 7
Digital Input Status | No Unit |  |  |  | I/O |  | Read | 6308 | 25352 | 4 | 1 | 4
Reserved | [7 empty] | 630C | 25356 | 12 | 1 | 12
Input Counter | No Unit |  |  |  | I/O |  | Read | 6318 | 25368 | 1 | 4 | 4
Reserved | [7 empty] | 631C | 25372 | 484 | 1 | 484
Errors Logs: Get Next | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Write | 6500 | 25856 | 1 | 1 | 1
Errors Logs: Entry Number | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Read/Write | 6501 | 25857 | 1 | 1 | 1
Reserved | [7 empty] | 6502 | 25858 | 5 | 1 | 5
Errors Logs: Direction | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Read/Write | 6507 | 25863 | 1 | 1 | 1
Reserved | [7 empty] | 6508 | 25864 | 8 | 1 | 8
Error Logs: Data Block | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Read | 6510 | 25872 | 1 | 105 | 105
Reserved | [7 empty] | 6579 | 25977 | 55 | 1 | 55
Alarms Logs: Get Next | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Write | 65B0 | 26032 | 1 | 1 | 1
Alarms Logs: Entry Number | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Read/Write | 65B1 | 26033 | 1 | 1 | 1
Reserved | [7 empty] | 65B2 | 26034 | 5 | 1 | 5
Alarms Logs: Direction | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Read/Write | 65B7 | 26039 | 1 | 1 | 1
Reserved | [7 empty] | 65B8 | 26040 | 8 | 1 | 8
Alarms Logs: Data Block | No Unit |  |  | Alligned with M4M | Notifications | Unsigned | Read/Write | 65C0 | 26048 | 1 | 105 | 105
Reserved | [7 empty] | 6629 | 26153 | 55 | 1 | 55
Audit Logs: Get Next | No Unit |  |  |  | Notifications | Unsigned | Write | 6660 | 26208 | 1 | 1 | 1
Audit Logs: Entry Number | No Unit |  |  |  | Notifications | Unsigned | Read/write | 6661 | 26209 | 1 | 1 | 1
Reserved | [7 empty] | 6662 | 26210 | 5 | 1 | 5
Audit Logs: Direction | No Unit |  |  |  | Notifications | Unsigned | Read/write | 6667 | 26215 | 1 | 1 | 1
Reserved | [7 empty] | 6668 | 26216 | 8 | 1 | 8
Audit Logs: Data Block | No Unit |  |  |  | Notifications | Unsigned | Read | 6670 | 26224 | 68 | 1 | 68
Reserved | [7 empty] | 66B4 | 26292 | 92 | 1 | 92
Warnings Logs: Get Next | No Unit |  |  |  | Notifications | Unsigned | Read | 6710 | 26384 | 1 | 1 | 1
Warnings Logs: Entry Number | No Unit |  |  |  | Notifications | Unsigned | Read/Write | 6711 | 26385 | 1 | 1 | 1
Reserved | [7 empty] | 6712 | 26386 | 5 | 1 | 5
Warnings Logs: Direction | No Unit |  |  |  | Notifications | Unsigned | Read/Write | 6717 | 26391 | 1 | 1 | 1
Reserved | [7 empty] | 6718 | 26392 | 8 | 1 | 8
Warnings Logs: Data Block | No Unit |  |  |  | Notifications | Unsigned | Read | 6720 | 26400 | 1 | 105 | 105
Reserved | [7 empty] | 6789 | 26505 | 8567 | 1 | 8567
Serial Number | No Unit |  |  |  | Device Info | Unsigned | Read | 8900 | 35072 | 2 | 1 | 2
Reserved | [7 empty] | 8902 | 35074 | 6 | 1 | 6
Firmware Version | No Unit |  |  |  | Device Info | Unsigned | Read | 8908 | 35080 | 1 | 8 | 8
Modbus Mapping Version | No Unit |  |  |  | Device Info | Unsigned | Read | 8910 | 35088 | 1 | 2 | 2
Reserved | [7 empty] | 8912 | 35090 | 1 | 78 | 78
Type Designation | No Unit |  |  |  | Device Info | Unsigned | Read | 8960 | 35168 | 1 | 6 | 6
Reserved | [7 empty] | 8966 | 35174 | 161 | 1 | 161
Current Active Tariff | No Unit |  |  |  | Tariff | Unsigned | Read | 8A07 | 35335 | 1 | 1 | 1
Reserved | [7 empty] | 8A08 | 35336 | 508 | 1 | 508
Current Transfomer Ratio Numerator | No Unit |  |  |  | Installation |  | Read/Write | 8C04 | 35844 | 1 | 2 | 2
Voltage Transfomer Ratio Numerator | No Unit |  |  |  | Installation |  | Read/Write | 8C06 | 35846 | 1 | 2 | 2
Current Transfomer Ratio Denominator | No Unit |  |  |  | Installation |  | Read/Write | 8C08 | 35848 | 1 | 2 | 2
Voltage Transfomer Ratio Denominator | No Unit |  |  |  | Installation |  | Read/Write | 8C0A | 35850 | 1 | 2 | 2
Function I/O Port 1 | No Unit |  |  |  | Installation |  | Read | 8C0C | 35852 | 1 | 1 | 1
Function I/O Port 2 | No Unit |  |  |  | Installation |  | Read | 8C0D | 35853 | 1 | 1 | 1
Function I/O Port 3 | No Unit |  |  |  | Installation |  | Read | 8C0E | 35854 | 1 | 1 | 1
Function I/O Port 4 | No Unit |  |  |  | Installation |  | Read | 8C0F | 35855 | 1 | 1 | 1
Pulse Output configuration Enable | No Unit |  |  | Alligned with M4M | I/O |  | Read/Write | 8C10 | 35856 | 1 | 1 | 1
Pulse Output Configuration Block | No Unit |  |  | Alligned with M4M | I/O |  | Read/Write | 8C11 | 35857 | 1 | 5 | 5
Set Pulse Input At Port | No Unit |  |  | Alligned with M4M | I/O |  | Read/Write | 8C16 | 35862 | 1 | 1 | 1
Set Output Always ON | No Unit |  |  | Alligned with M4M | I/O |  | Read/Write | 8C17 | 35863 | 1 | 1 | 1
Set Output Always OFF | No Unit |  |  | Alligned with M4M | I/O |  | Read/Write | 8C18 | 35864 | 1 | 1 | 1
Set Output Via Communication | No Unit |  |  | Alligned with M4M | I/O |  | Read/Write | 8C19 | 35865 | 1 | 1 | 1
Reserved | [7 empty] | 8C1A | 35866 | 1 | 1 | 70
Alarm Instance / Set Alarm To Output | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C60 | 35936 | 1 | 1 | 1
Alarm Measurement Parameter | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C61 | 35937 | 1 | 1 | 1
Alarm Threshold | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C62 | 35938 | 1 | 4 | 4
Alarm Hysteresis | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C66 | 35942 | 1 | 1 | 1
Alarm Delay | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C67 | 35943 | 1 | 1 | 1
Alarm Type | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C68 | 35944 | 1 | 1 | 1
Alarm Action | No Unit |  |  | Alligned with M4M | Alarm |  | Read/Write | 8C69 | 35945 | 1 | 2 | 2
Reserved | [7 empty] | 8C6B | 35947 | 37 | 1 | 37
Tariff Source | No Unit |  |  |  | Tariff |  |  | 8C90 | 35984 | 1 | 1 | 1
Input Configuration | No Unit |  |  |  | Tariff |  |  | 8C91 | 35985 | 1 | 2 | 2
Reserved | [7 empty] | 8C93 | 35987 | 77 | 1 | 77
CO2 Conversion Factor | No Unit |  | 0.001 |  | Configuration |  | Read/Write | 8CE0 | 36064 | 1 | 2 | 2
Currency Conversion Factor | No Unit |  | 0.01 |  | Configuration |  | Read/Write | 8CE2 | 36066 | 1 | 2 | 2
Led Source | No Unit |  |  |  | Configuration |  | Read/Write | 8CE4 | 36068 | 1 | 1 | 1
Wiring Setting | No Unit |  |  | Instead of "number of elements" | Installation |  | Read/Write | 8CE5 | 36069 | 1 | 1 | 1
Note on F136: [Threaded comment] Your version of Excel allows you to read this threaded comment; however, any edits to it will get removed if the file is opened in a newer version of Excel. Learn more: https://go.microsoft.com/fwlink/?linkid=870924 Comment: Please, add details