## External Modbus Map (Customer)
Parameter | Unit | Details | Resolution | Data Type | Access | Register (Hex) | Register (Dec) | Nr of registers | Size | Product Type
Internal communication failure | none | 0xFF00 = failure / 0x0000 = OK | none | Unsigned | Read | 0x8000 | 32768 | 1 | 1 | All version
Command breaker | none | 0xFF00 = close / 0x0000 = open | none | Unsigned | Read/Write | 0x8001 | 32769 | 1 | 1 | All version
Enable/Disable remote input control | none | 0xFF00 = enable (default value) / 0x0000 = disable | none | Unsigned | Read/Write | 0x8002 | 32770 | 1 | 1 | MOD - ARI - ARI30
Enable/Disable opening/closing command via communication | none | 0xFF00 = enable (default value) / 0x0000 = disable | none | Unsigned | Read/Write | 0x8003 | 32771 | 1 | 1 | All version
Reclosing attempts | none | From 1 to 10; (3 = default value) | none | Unsigned | Read/Write | 0x8004 | 32772 | 1 | 1 | ARI / ARI30
Waiting time amoung reclosing | seconds | From 1 to 60; (ARI default value = 3) (ARI-30 default value = 30) | none | Unsigned | Read/Write | 0x8005 | 32773 | 1 | 1 | ARI / ARI30
Neutralization time | seconds | 12 second default value for ARI-ARI30 and 45 seconds for ARH | none | Unsigned | Read/Write | 0x8006 | 32774 | 1 | 1 | ARI / ARI30 / ARH
Update mode (use for FW Upgrade, opening/closing disabled) | none | 0xFF00 = Update mode enable / 0x0000 = Update mode disable (default) | none | Unsigned | Read/Write | 0x8007 | 32775 | 1 | 1 | All version
Status breaker | none | 0xFF00 = close, 0x0000 = open | none | Unsigned | Read | 0x8008 | 32776 | 1 | 1 | All version
Tripped | none | 0xFF00 = trip, 0x0000 = no trip. When a trip occur, register fill with 0xFF00, after reclosing operation register fill with 0x0000. | none | Unsigned | Read | 0x8009 | 32777 | 1 | 1 | All version
Time (Tripped) |  | YYMMDD:HHMMSS Date and Time of the last trip condition |  |  | Read | 0x800A | 32778 | 3 | 3 | All version
Peak current | mA | Max peak current during last maneuver | none | Unsigned | Read | 0x800D | 32781 | 1 | 1 | All version
Motor torque | mN-m | Max value during last maneuver | none | Unsigned | Read | 0x800E | 32782 | 1 | 1 | All version
Time to max torque | millisecond | Time to reach max torque | none | Unsigned | Read | 0x800F | 32783 | 1 | 1 | All version
Peak torque Toggle angle | degree angle | Angle @ peak torque | none | Unsigned | Read | 0x8010 | 32784 | 1 | 1 | All version
Close time | millisecond | Time to complete last closing maneuver | none | Unsigned | Read | 0x8011 | 32785 | 1 | 1 | All version
Open time | millisecond | Time to complete last opening maneuver | none | Unsigned | Read | 0x8012 | 32786 | 1 | 1 | All version
Total number of maneuver (closing + opening) | none | Max number 20.000 | none | Unsigned | Read | 0x8013 | 32787 | 1 | 1 | All version
Total number of closing maneuver | none |  | none | Unsigned | Read | 0x8014 | 32788 | 1 | 1 | All version
Maneuver (open or close) attempt ongoing | none | 0xFF00 = ongoing, 0x0000 = no maneuver attempt ongoing | none | Unsigned | Read | 0x8015 | 32789 | 1 | 1 | All version
Assessment attempt ongoing | none | 0xFF00 = ongoing, 0x0000 = not ongoing | none | Unsigned | Read | 0x8016 | 32790 | 1 | 1 | ARH
Result of the last assessment | none | 0x0000 = pass, 0xFF00 = fail, 0xA5A5 = no assessment performed | none | Unsigned | Read | 0x8017 | 32791 | 1 | 1 | ARH
Assessment Parameter Temp | °C | Temperature value during assessment | TBD | Unsigned | Read | 0x8018 | 32792 | 1 | 1 | ARH
Assessment Parameter Voltage | Volt | Voltage value during assessment | TBD | Unsigned | Read | 0x8019 | 32793 | 1 | 1 | ARH
Assessment Parameter PhRd | none | Phase that fails during assessment | none | Unsigned | Read | 0x801A | 32794 | 1 | 1 | ARH
Assessment Parameter Rd | Ohm | Rd value | TBD | Unsigned | Read | 0x801B | 32795 | 1 | 1 | ARH
Output 1 state | none | 0xFF00 = MOD lever close, 0x0000 = MOD lever open | none | Unsigned | Read | 0x801C | 32796 | 1 | 1 | All version
Output 2 state | none | 0xFF00 = lock state/standby active, 0x0000 = lock-out state not active | none | Unsigned | Read | 0x801D | 32797 | 1 | 1 | All version
Input 1 state | none | 0xFF00 = active, 0x0000 = not active | none | Unsigned | Read | 0x801E | 32798 | 1 | 1 | MOD - ARI - ARI30
Input 2 state | none | 0xFF00 = active, 0x0000 = not active | none | Unsigned | Read | 0x801F | 32799 | 1 | 1 | MOD - ARI - ARI30
Power fail date/time | none | YYMMDD:HHMMSS Date and Time of the last power fail condition | none |  | Read | 0x8020 | 32800 | 3 | 3 | All version
Last demanded command not completed due to power fail | none | 0xFF00 = close, 0x0000 = open, 0xA5A5 = all command completed | none | Unsigned | Read | 0x8023 | 32803 | 1 | 1 | All version
MOD / ARI / ARI30 / ARH diagnostic register | none | MOD device status | none | Unsigned | Read | 0x8024 | 32804 | 1 | 1 | All version
|  | Device Status Active: (0 = default value; 1 = active) | Bit 0 |  |  | Bit 0 of 0x8024 |  | 0
|  | Device Status Not Active: (0 = default value; 1 = not active) | Bit 1 |  |  | Bit 1 of 0x8024 |  | 0
|  | Device in Lock-out state (0 = default value; 1 = lock-out) | Bit 2 |  |  | Bit 2 of 0x8024 |  | 0
|  | "Dead time" during the standby mode (0 = default value; 1 = not active) | Bit 3 |  |  | Bit 3 of 0x8024 |  | 0
|  | Fault condition - motor driver: (0 = default value; 1 = fault condition) | Bit 4 |  |  | Bit 4 of 0x8024 |  | 0
|  | Device Fault condition - device error : (0 = default value; 1 = fault condition) | Bit 5 |  |  | Bit 5 of 0x8024 |  | 0
Product type number ID MOD / ARI / ARI30 / ARH | none | See Product type details sheet | none |  | Read | 0x8025 | 32805 | 1 | 1 | All version
Product type number ID COMM | none | See Product type details sheet | none |  | Read | 0x8026 | 32806 | 1 | 1 | All version
Product type MOD / ARI / ARI30 / ARH | none | See Product type details sheet | none | ASCII | Read | 0x8027 | 32807 | 8 | 8 | All version
Product type COMM | none | See Product type details sheet | none | ASCII | Read | 0x802F | 32815 | 8 | 8 | All version
Serial number MOD / ARI / ARI30 / ARH | none | Format e.g. M086AB1000 | none | ASCII | Read | 0x8037 | 32823 | 5 | 5 | All version
Serial number COMM | none | Format e.g. M086AB1001 | none | ASCII | Read | 0x803C | 32828 | 5 | 5 | All version
FW version MOD / ARI / ARI30 / ARH | none |  | none | ASCII | Read | 0x8041 | 32833 | 2 | 2 | All version
FW version COMM | none |  | none | ASCII | Read | 0x8043 | 32835 | 2 | 2 | All version
Date/Time last successfull FW update MOD / ARI / ARI30 / ARH | none | YYMMDD:HHMMSS | none |  | Read | 0x8045 | 32837 | 3 | 3 | All version
Date/Time last successfull FW update COMM | none | YYMMDD:HHMMSS | none |  | Read | 0x8048 | 32840 | 3 | 3 | All version
Date Time (read only for Wi-Fi module) | none | YYMMDD:HHMMSS | none |  | Read/Write | 0x804B | 32843 | 3 | 3 | All version
Modbus RTU parameter Slave Address | none | Address: 1 - 247 | none | Unsigned | Read/Write | 0x804E | 32846 | 1 | 1 | All version
Modbus RTU parameter Baud Rate | none | Baudrate: 2400, 4800, 9600, 19200, 38400, 57600, 115200 | none | Unsigned | Read/Write | 0x804F | 32847 | 2 | 2 | All version
Modbus RTU parameter Parity | none | Parity: 2- none; 1-even; 0- odd | none | Unsigned | Read/Write | 0x8051 | 32849 | 1 | 1 | All version
EVENT LOG
Entry count | none | Total number of entries in event log (<-1> in case of the functionality failure) | 1 | Signed | Read | 0x8100 | 33024 | 1 | N/A | All versions
Selected entry | none | Requested entry to view (from <0> to <entry count - 1>; <0> = the newset entry) | 1 | Unsigned | Read/Write | 0x8101 | 33025 | 1 | N/A | All versions
Entry | N/A | Entry data | N/A | N/A | Read | 0x8102 | 33026 | 5 | N/A | All versions
| none | Event No. (from <0> to <65 535>, then overlaps again to <0>) | N/A | Unsigned |  |  |  |  | 1
| none | Event date time YYMM | N/A | Unsigned |  |  |  |  | 1
| none | Event date time DDHH | N/A | Unsigned |  |  |  |  | 1
| none | Event date time MMSS | N/A | Unsigned |  |  |  |  | 1
| none | Event type ID (See Event type details sheet) | N/A | Unsigned |  |  |  |  | 1
Report slave ID - dedicated modbus function 17 - shall be available

## Internal Modbus Map
Parameter | Unit | Details | Resolution | Data Type | Access | Register (Hex) | Register (Dec) | Nr of registers | Size | Product Type | Device responsible to fill the register value (Provided by)
STATUS TELEGRAM From MOD To COMM via Write Multiple Register Modbus function
Status breaker | none | 0xFF00 = close, 0x0000 = open | none | Unsigned | Read | 0x8200 | 33280 | 1 | 1 | All version | MOD
Tripped | none | 0xFF00 = trip, 0x0000 = no trip. When a trip occur, register fill with 0xFF00, after reclosing operation register fill with 0x0000. | none | Unsigned | Read | 0x8201 | 33281 | 1 | 1 | All version | MOD
Peak current | mA | Max peak current during last maneuver | none | Unsigned | Read | 0x8202 | 33282 | 1 | 1 | All version | MOD
Motor torque | mN-m | Max value during last maneuver | none | Unsigned | Read | 0x8203 | 33283 | 1 | 1 | All version | MOD
Time to max torque | millisecond | Time to reach max torque | none | Unsigned | Read | 0x8204 | 33284 | 1 | 1 | All version | MOD
Peak torque Toggle angle | degree angle | Angle @ peak toreque | none | Unsigned | Read | 0x8205 | 33285 | 1 | 1 | All version | MOD
Close time | millisecond | Time to complete last closing maneuver | none | Unsigned | Read | 0x8206 | 33286 | 1 | 1 | All version | MOD
Open time | millisecond | Time to complete last opening maneuver | none | Unsigned | Read | 0x8207 | 33287 | 1 | 1 | All version | MOD
Total number of maneuver (closing + opening) | none | Max number 20.000 | none | Unsigned | Read | 0x8208 | 33288 | 1 | 1 | All version | MOD
Total number of closing maneuver | none |  | none | Unsigned | Read | 0x8209 | 33289 | 1 | 1 | All version | MOD
Maneuver (open or close) attempt ongoing | none | 0xFF00 = ongoing, 0x0000 = no maneuver attempt ongoing | none | Unsigned | Read | 0x820A | 33290 | 1 | 1 | All version | MOD
Assessment attempt ongoing | none | 0xFF00 = ongoing, 0x0000 = not ongoing | none | Unsigned | Read | 0x820B | 33291 | 1 | 1 | All version | MOD
Result of the last assessment | none | 0x0000 = pass, 0xFF00 = fail, 0xA5A5 = no assessment performed | none | Unsigned | Read | 0x820C | 33292 | 1 | 1 | All version | MOD (MOD receive from ARH and forward to COMM module)
Output 1 state | none | 0xFF00 = MOD lever close, 0x0000 = MOD lever open | none | Unsigned | Read | 0x820D | 33293 | 1 | 1 | All version | MOD
Output 2 state | none | 0xFF00 = lock state/standby active, 0x0000 = lock-out state not active | none | Unsigned | Read | 0x820E | 33294 | 1 | 1 | All version | MOD
Input 1 state | none | 0xFF00 = active, 0x0000 = not active | none | Unsigned | Read | 0x820F | 33295 | 1 | 1 | All version | MOD
Input 2 state | none | 0xFF00 = active, 0x0000 = not active | none | Unsigned | Read | 0x8210 | 33296 | 1 | 1 | All version | MOD
Last demanded command not completed due to power fail | none | 0xFF00 = close, 0x0000 = open, 0xA5A5 = all command completed | none | Unsigned | Read | 0x8211 | 33297 | 1 | 1 | All version | MOD
MOD diagnostic register | none | MOD device status | none | Unsigned | Read | 0x8212 | 33298 | 1 | 1 | All version | MOD
|  | Device Status Active: (0 = default value; 1 = active) | Bit 0 |  |  | Bit 0 of 0x8212 |  | 0 |  | All version
|  | Device Status Not Active: (0 = default value; 1 = not active) | Bit 1 |  |  | Bit 1 of 0x8212 |  | 0 |  | All version
|  | Device in Lock-out state (0 = default value; 1 = lock-out) | Bit 2 |  |  | Bit 2 of 0x8212 |  | 0 |  | All version
|  | "Dead time" during the standby mode (0 = default value; 1 = not active) | Bit 3 |  |  | Bit 3 of 0x8212 |  | 0 |  | All version
|  | Fault condition - motor driver: (0 = default value; 1 = fault condition) | Bit 4 |  |  | Bit 4 of 0x8212 |  | 0 |  | All version
|  | Device Fault condition - device error : (0 = default value; 1 = fault condition) | Bit 5 |  |  | Bit 5 of 0x88CE |  | 0 |  | All version
Product type number ID MOD - ARI ARI30 - ARH | none | See Product type details sheet | none |  | Read | 0x8213 | 33299 | 1 | 1 | All version | MOD
Product type MOD - ARI ARI30 - ARH | none | See Product type details sheet | none | ASCII | Read | 0x8214 | 33300 | 8 | 8 | All version | MOD
Serial number(s) MOD - ARI ARI30 - ARH | none | Format e.g. M086AB1000 | none | ASCII | Read | 0x821C | 33308 | 5 | 5 | All version | MOD
FW version MOD - ARI - ARI30 - ARH module | none |  | none | ASCII | Read | 0x8221 | 33313 | 2 | 2 | All version | MOD
Assessment Parameter Temp | °C | Temperature value | TBC | Unsigned | Read | 0x8223 | 33315 | 1 | 1 | ARH | MOD (MOD receive from ARH and forward to COMM module)
Assessment Parameter Voltage | Volt | Voltage value | TBC | Unsigned | Read | 0x8224 | 33316 | 1 | 1 | ARH | MOD (MOD receive from ARH and forward to COMM module)
Assessment Parameter PhRd | none | Phase that fails during assessment | none | Unsigned | Read | 0x8225 | 33317 | 1 | 1 | ARH | MOD (MOD receive from ARH and forward to COMM module)
Assessment Parameter Rd | Ohm | Rd value | TBC | Unsigned | Read | 0x8226 | 33318 | 1 | 1 | ARH | MOD (MOD receive from ARH and forward to COMM module)
39
COMMAND TELEGRAM From MOD To COMM via Read Holding Register Modbus function
Command breaker | none | 0xFF00 = close; 0x0000 = open; 0xA5A5 = no command (default value); On internal communication COMM module send to the MOD always the value 0xA5A5 and just in case a command shall be executed it valorize the register with 0xFF00 or 0x0000 then after 100 mS, it come back to send the value 0xA5A5 = no command. | none | Unsigned | Read/Write | 0x8000 | 32768 | 1 | 1 | All version | COMM
Enable/Disable remote input control | none | 0xFF00 = enable (default value) / 0x0000 = disable | none | Unsigned | Read/Write | 0x8001 | 32769 | 1 | 1 | All version | COMM
Enable/Disable opening/closing command via communication | none | 0xFF00 = enable (default value) / 0x0000 = disable | none | Unsigned | Read/Write | 0x8002 | 32770 | 1 | 1 | All version | COMM
Reclosing attempts | none | From 1 to 10; (3 = default value) | none | Unsigned | Read/Write | 0x8003 | 32771 | 1 | 1 | All version | COMM
Waiting time amoung reclosing | seconds | From 1 to 60; (ARI default value = 3) (ARI-30 default value = 30) | none | Unsigned | Read/Write | 0x8004 | 32772 | 1 | 1 | All version | COMM
Neutralization time | seconds | 12 second default value for ARI-ARI30 and 45 seconds for ARH | none | Unsigned | Read/Write | 0x8005 | 32773 | 1 | 1 | All version | COMM
Update mode (use for FW Upgrade, opening/closing disabled) | none | 0xFF00 = Update mode enable / 0x0000 = Update mode disable (default) | none | Unsigned | Read/Write | 0x8006 | 32774 | 1 | 1 | All version | COMM
FW Upgrade starts for MOD device | none | 0xFF00 = FW upgrade enable / 0x0000 = FW upgrade disable (default) When MOD send the FW upgrade result, then COMM reset this register to 0x0000 | none | Unsigned | Read/Write | 0x8007 | 32775 | 1 | 1 | All version | COMM
FW Upgrade starts for ARH device | none | 0xFF00 = FW upgrade enable / 0x0000 = FW upgrade disable (default) When MOD send the FW upgrade result, then COMM reset this register to 0x0000 | none | Unsigned | Read/Write | 0x8008 | 32776 | 1 | 1 | All version | COMM
FW UPGRADE TELEGRAM From MOD To COMM
Number of data packages (Read Holding Register) | none | Number of packages to be transferred | none | Unsigned | Read | 0x2000 | 8192 | 1 | 1 | All version | COMM
FW upgrade process result (Write Single Register) | none | result: 0x0000 = success; 0xFF00= fails | none | Unsigned | Write | 0x2001 | 8193 | 1 | 1 | All version | MOD
Packages selection (Write Single Register) | none | MOD request to the COMM: which package needs | none | Unsigned | Read/Write | 0x2002 | 8194 | 1 | 1 | All version | MOD
Data packages receiving (Read Holding Register) | none | We want to be transferred a packages with size of 128 bytes so this means 64 modbus register | none | Unsigned | Read | 0x2100 | 8448 | 1 | 1 | All version | COMM
ARH TELEGRAM From MOD To ARH
ARH FW upgrade status (Write Single Register) | none | 0x0000 = Not ongoing / 0x0001 = Start / 0x0002 = End | none | Unsigned | Write | 0x8102 | 33026 | 1 | 1 | ARH | ARH
S3 status switch (Read Holding Register) | none | 0xFF00 = Arh device active, 0x0000 = Arh device not active | none | Unsigned | Read | 0x8103 | 33027 | 1 | 1 | ARH | ARH
Assessment result (Read Holding Register) | none | 0xFF00 = Result Negative + stop / 0x0000 = Result Positive(reclose) + stop/ 0xA5A5 = On going assessment + movement / 0xA500 On going assessment + stop / 0x00A5 Start assessment | none | Unsigned | Read | 0x8104 | 33028 | 1 | 1 | ARH | ARH
Assessment Parameter Temp | none |  | none | Unsigned | Read | 0x8105 | 33029 | 1 | 1 | ARH | ARH
Assessment Parameter Voltage | none |  | none | Unsigned | Read | 0x8106 | 33030 | 1 | 1 | ARH | ARH
Assessment Parameter PhRd | none |  | none | Unsigned | Read | 0x8107 | 33031 | 1 | 1 | ARH | ARH
Assessment Parameter Rd | none |  | none | Unsigned | Read | 0x8108 | 33032 | 1 | 1 | ARH | ARH
FW upgrade process result (Read Holding Register) | none | result: 0x0000 = success; 0xFF00= fails | none | Unsigned | Read | 0x2001 | 8193 | 1 | 1 | All version | ARH
Data packages receiving (Write Multiple Registers) | none | We want to be transferred a packages with size of 128 bytes so this means 64 modbus register | none | Unsigned | Write | 0x2100 | 8448 | 64 | 128 | All version | MOD
MOD PCBA PRODUCTION TELEGRAM E2 PARAMETERS
Peak current close |  |  |  | Unsigned | Write | 0x9000 | 36864 | 1 | 1 | PCBA MOD | Production Tool
Peak current open |  |  |  | Unsigned | Write | 0x9001 | 36865 | 1 | 1 | PCBA MOD | Production Tool
Peak current stopping |  |  |  | Unsigned | Write | 0x9002 | 36866 | 1 | 1 | PCBA MOD | Production Tool
Peak current arh |  |  |  | Unsigned | Write | 0x9003 | 36867 | 1 | 1 | PCBA MOD | Production Tool
Return angle close |  |  |  | Unsigned | Write | 0x9004 | 36868 | 1 | 1 | PCBA MOD | Production Tool
Return angle open |  |  |  | Unsigned | Write | 0x9005 | 36869 | 1 | 1 | PCBA MOD | Production Tool
Arh angle close |  |  |  | Unsigned | Write | 0x9006 | 36870 | 1 | 1 | PCBA MOD | Production Tool
Arh angle open |  |  |  | Unsigned | Write | 0x9007 | 36871 | 1 | 1 | PCBA MOD | Production Tool
Timer operation |  |  |  | Unsigned | Write | 0x9008 | 36872 | 1 | 1 | PCBA MOD | Production Tool
Timer force open |  |  |  | Unsigned | Write | 0x9009 | 36873 | 1 | 1 | PCBA MOD | Production Tool
Setpoint close |  |  |  | Unsigned | Write | 0x900A | 36874 | 1 | 1 | PCBA MOD | Production Tool
Setpoint open |  |  |  | Unsigned | Write | 0x900B | 36875 | 1 | 1 | PCBA MOD | Production Tool
Setpoint arh |  |  |  | Unsigned | Write | 0x900C | 36876 | 1 | 1 | PCBA MOD | Production Tool
Setpoint return |  |  |  | Unsigned | Write | 0x900D | 36877 | 1 | 1 | PCBA MOD | Production Tool
Setpoint stopping |  |  |  | Unsigned | Write | 0x900E | 36878 | 1 | 1 | PCBA MOD | Production Tool
Max PID error |  |  |  | Unsigned | Write | 0x900F | 36879 | 1 | 1 | PCBA MOD | Production Tool
PWM 9 Volt |  |  |  | Unsigned | Write | 0x9010 | 36880 | 1 | 1 | PCBA MOD | Production Tool
PWM 12 Volt |  |  |  | Unsigned | Write | 0x9011 | 36881 | 1 | 1 | PCBA MOD | Production Tool
Kp coefficient |  |  |  | Unsigned | Write | 0x9012 | 36882 | 1 | 1 | PCBA MOD | Production Tool
Ki coefficient |  |  |  | Unsigned | Write | 0x9013 | 36883 | 1 | 1 | PCBA MOD | Production Tool
Kd coefficient |  |  |  | Unsigned | Write | 0x9014 | 36884 | 1 | 1 | PCBA MOD | Production Tool
Q coefficient Kalman filter |  |  |  | Unsigned | Write | 0x9015 | 36885 | 1 | 1 | PCBA MOD | Production Tool
R coefficient Kalman filter |  |  |  | Unsigned | Write | 0x9016 | 36886 | 1 | 1 | PCBA MOD | Production Tool
Motor direction |  |  |  | Unsigned | Write | 0x9017 | 36887 | 1 | 1 | PCBA MOD | Production Tool
Dead angle |  |  |  | Unsigned | Write | 0x9018 | 36888 | 1 | 1 | PCBA MOD | Production Tool
MOD PCBA PRODUCTION TELEGRAM E2 REGISTERS
Status breaker |  |  |  | Unsigned | Write | 0x9100 | 37120 | 1 | 1 | PCBA MOD | Production Tool
Tripped |  |  |  | Unsigned | Write | 0x9101 | 37121 | 1 | 1 | PCBA MOD | Production Tool
Peak current |  |  |  | Unsigned | Write | 0x9102 | 37122 | 1 | 1 | PCBA MOD | Production Tool
Motor torque |  |  |  | Unsigned | Write | 0x9103 | 37123 | 1 | 1 | PCBA MOD | Production Tool
Time to max torque |  |  |  | Unsigned | Write | 0x9104 | 37124 | 1 | 1 | PCBA MOD | Production Tool
Peak torque Toggle angle |  |  |  | Unsigned | Write | 0x9105 | 37125 | 1 | 1 | PCBA MOD | Production Tool
Close time |  |  |  | Unsigned | Write | 0x9106 | 37126 | 1 | 1 | PCBA MOD | Production Tool
Open time |  |  |  | Unsigned | Write | 0x9107 | 37127 | 1 | 1 | PCBA MOD | Production Tool
Total number of maneuver (closing + opening) |  |  |  | Unsigned | Write | 0x9108 | 37128 | 1 | 1 | PCBA MOD | Production Tool
Total number of closing maneuver |  |  |  | Unsigned | Write | 0x9109 | 37129 | 1 | 1 | PCBA MOD | Production Tool
Maneuver (open or close) attempt ongoing |  |  |  | Unsigned | Write | 0x910A | 37130 | 1 | 1 | PCBA MOD | Production Tool
Assessent attempt ongoing |  |  |  | Unsigned | Write | 0x910B | 37131 | 1 | 1 | PCBA MOD | Production Tool
Result of the last assessment |  |  |  | Unsigned | Write | 0x910C | 37132 | 1 | 1 | PCBA MOD | Production Tool
Output 1 state |  |  |  | Unsigned | Write | 0x910D | 37133 | 1 | 1 | PCBA MOD | Production Tool
Output 2 state |  |  |  | Unsigned | Write | 0x910E | 37134 | 1 | 1 | PCBA MOD | Production Tool
Input 1 |  |  |  | Unsigned | Write | 0x910F | 37135 | 1 | 1 | PCBA MOD | Production Tool
Input 2 |  |  |  | Unsigned | Write | 0x9110 | 37136 | 1 | 1 | PCBA MOD | Production Tool
Last demanded command not completed due to power fail |  |  |  | Unsigned | Write | 0x9111 | 37137 | 1 | 1 | PCBA MOD | Production Tool
MOD diagnostic register |  |  |  | Unsigned | Write | 0x9112 | 37138 | 1 | 1 | PCBA MOD | Production Tool
Product type number ID MOD - ARI - ARI30 - ARH |  |  |  | Unsigned | Write | 0x9113 | 37139 | 1 | 1 | PCBA MOD | Production Tool
Product type MOD - ARI - ARI30 - ARH |  |  |  | Unsigned | Write | 0x9114 | 37140 | 8 | 8 | PCBA MOD | Production Tool
Serial number(s) MOD - ARI - ARI30 - ARH |  |  |  | Unsigned | Write | 0x911C | 37148 | 5 | 5 | PCBA MOD | Production Tool
FW version MOD - ARI - ARI30 - ARH module |  |  |  | Unsigned | Write | 0x9121 | 37153 | 2 | 2 | PCBA MOD | Production Tool
assessmentTemp |  |  |  | Unsigned | Write | 0x9123 | 37155 | 1 | 1 | PCBA MOD | Production Tool
assessmentVoltage |  |  |  | Unsigned | Write | 0x9124 | 37156 | 1 | 1 | PCBA MOD | Production Tool
assessmentPhRd |  |  |  | Unsigned | Write | 0x9125 | 37157 | 1 | 1 | PCBA MOD | Production Tool
assessmentRd |  |  |  | Unsigned | Write | 0x9126 | 37158 | 1 | 1 | PCBA MOD | Production Tool
Command Breaker |  |  |  | Unsigned | Write | 0x9127 | 37159 | 1 | 1 | PCBA MOD | Production Tool
Old command breaker |  |  |  | Unsigned | Write | 0x9128 | 37160 | 1 | 1 | PCBA MOD | Production Tool
Lever position |  |  |  | Unsigned | Write | 0x9129 | 37161 | 1 | 1 | PCBA MOD | Production Tool
Enable/Disable remote input control |  |  |  | Unsigned | Write | 0x912A | 37162 | 1 | 1 | PCBA MOD | Production Tool
Enable/Disable opening/closing command via communication |  |  |  | Unsigned | Write | 0x912B | 37163 | 1 | 1 | PCBA MOD | Production Tool
Reclosing attempts |  |  |  | Unsigned | Write | 0x912C | 37164 | 1 | 1 | PCBA MOD | Production Tool
Waiting time amoung reclosing |  |  |  | Unsigned | Write | 0x912D | 37165 | 1 | 1 | PCBA MOD | Production Tool
Neutralization time |  |  |  | Unsigned | Write | 0x912E | 37166 | 1 | 1 | PCBA MOD | Production Tool
Outputs Configuration |  |  |  | Unsigned | Write | 0x912F | 37167 | 1 | 1 | PCBA MOD | Production Tool
48
MOD & ARH PCBA PRODUCTION TELEGRAM LOCK DEVICE
Lock Device | none | Use to lock (0xA5A5) / unlock (0x5A5A) device |  | Unsigned | Write | 0x9200 | 37376 | 1 | 1 | PCBA MOD and ARH | Production Tool
MOD PCBA PRODUCTION TELEGRAM TEST
Led |  | (0000)All leds Off (0001)Green led On (0002)Green led Off (0003)Red led On (0004)Red led Off (0005)All leds On |  | Unsigned | Read/Write | 0x9300 | 37632 | 1 | 1 | PCBA MOD | Production Tool
Output 1 |  | (0000) Output Off (0001) Output On |  | Unsigned | Read/Write | 0x9301 | 37633 | 1 | 1 | PCBA MOD | Production Tool
Output 2 |  | (0000) Output Off (0001) Output On |  | Unsigned | Read/Write | 0x9302 | 37634 | 1 | 1 | PCBA MOD | Production Tool
Input 1 status |  | (0000) Input released (0001) Input pressed |  | Unsigned | Read | 0x9303 | 37635 | 1 | 1 | PCBA MOD | Production Tool
Input 2 status |  | (0000) Input released (0001) Input pressed |  | Unsigned | Read | 0x9304 | 37636 | 1 | 1 | PCBA MOD | Production Tool
Switch 1 status |  | (0000) Switch not pressed - Off (0001) Switch pressed - On |  | Unsigned | Read | 0x9305 | 37637 | 1 | 1 | PCBA MOD | Production Tool
Switch 2 status |  | (0000) Switch not pressed - Off (0001) Switch pressed - On |  | Unsigned | Read | 0x9306 | 37638 | 1 | 1 | PCBA MOD | Production Tool
Switch 3 status |  | (0000) Switch not pressed - Off (0001) Switch pressed - On |  | Unsigned | Read | 0x9307 | 37639 | 1 | 1 | PCBA MOD | Production Tool
Optic Barrier |  | (0000) Optic barrier Off (0001) Optic barrier On |  | Unsigned | Read | 0x9308 | 37640 | 1 | 1 | PCBA MOD | Production Tool
Hall effect sensor |  | Angle values |  | Unsigned | Read | 0x9309 | 37641 | 1 | 1 | PCBA MOD | Production Tool
Driver motor |  | (0000) CW Motor (0001) CCW Motor |  | Unsigned | Write | 0x930A | 37642 | 1 | 1 | PCBA MOD | Production Tool
ARH PCBA PRODUCTION TELEGRAM TEST PCBA
Read Assessment |  | 0xFF00 = Result Negative + stop / 0x0000 = Result Positive(reclose) + stop/ 0xA5A5 = On going assessment + movement / 0xA500 On going assessment + stop |  | Unsigned | Read | 0x9400 | 37888 | 1 | 1 | PCBA ARH | Production Tool
Switch 1 status |  | (0000) Switch not pressed - Off (0001) Switch pressed - On |  | Unsigned | Read | 0x9401 | 37889 | 1 | 1 | PCBA ARH | Production Tool
Switch 2 status |  | (0000) Switch not pressed - Off (0001) Switch pressed - On |  | Unsigned | Read | 0x9402 | 37890 | 1 | 1 | PCBA ARH | Production Tool
Switch 3 status |  | (0000) Switch not pressed - Off (0001) Switch pressed - On |  | Unsigned | Read | 0x9403 | 37891 | 1 | 1 | PCBA ARH | Production Tool
ARH PRODUCTION TELEGRAM E2 REGISTERS
arhDeviceType |  | 0x0000 = 30mA 2P 0x0001 = 300 mA 2P 0x0002 = 30mA 4P 0x0003 = 300 mA 4P |  | Unsigned | Write | 9500 | 38144 | 1 | 1 | PCBA ARH | Production Tool
assessmentResult |  |  |  | Unsigned | Write | 9501 | 38145 | 1 | 1 | PCBA ARH | Production Tool
assessmentTemp |  |  |  | Unsigned | Write | 9502 | 38146 | 1 | 1 | PCBA ARH | Production Tool
assessmentVoltage |  |  |  | Unsigned | Write | 9503 | 38147 | 1 | 1 | PCBA ARH | Production Tool
assessmentPhRd |  |  |  | Unsigned | Write | 9504 | 38148 | 1 | 1 | PCBA ARH | Production Tool
assessmentRd |  |  |  | Unsigned | Write | 9505 | 38149 | 1 | 1 | PCBA ARH | Production Tool
switchS3Status |  |  |  | Unsigned | Write | 9506 | 38150 | 1 | 1 | PCBA ARH | Production Tool
fwVersionArh1 |  |  |  | Unsigned | Write | 9507 | 38151 | 1 | 1 | PCBA ARH | Production Tool
fwVersionArh2 |  |  |  | Unsigned | Write | 9508 | 38152 | 1 | 1 | PCBA ARH | Production Tool
vrmsConst30 |  |  |  | Unsigned | Write | 9509 | 38153 | 2 | 2 | PCBA ARH | Production Tool
vrmsVline30 |  |  |  | Unsigned | Write | 950A | 38154 | 2 | 2 | PCBA ARH | Production Tool
vrmsConst300 |  |  |  | Unsigned | Write | 950B | 38155 | 2 | 2 | PCBA ARH | Production Tool
vrmsVline300 |  |  |  | Unsigned | Write | 950C | 38156 | 2 | 2 | PCBA ARH | Production Tool
vlineConst |  |  |  | Unsigned | Write | 950D | 38157 | 2 | 2 | PCBA ARH | Production Tool
vlineVref |  |  |  | Unsigned | Write | 950E | 38158 | 2 | 2 | PCBA ARH | Production Tool
vlineVrefSec |  |  |  | Unsigned | Write | 950F | 38159 | 2 | 2 | PCBA ARH | Production Tool

## Product type details
Product type number ID | Product type | Details
0 | MOD | Motor Operating Device
1 | MOD LV | Motor Operating Device “Low Voltage”
2 | ARI | Automatic Reclosing Device for RCCBs without Id assessment
3 | ARI LV | Automatic Reclosing Device “Low Voltage” for RCCBs without Id assessment
4 | ARI-30 | Automatic Reclosing Device for RCCBs with 30s delay among attempts without Id assessment
5 | ARH 2P 30mA | Automatic Reclosing Device for 2P RCCBs with Id assessment for 30mA Idn
6 | ARH 2P 300mA | Automatic Reclosing Device for 2P RCCBs with Id assessment for 300mA Idn
7 | ARH 4P 30mA | Automatic Reclosing Device for 4P RCCBs with Id assessment for 30mA Idn
8 | ARH 4P 300mA | Automatic Reclosing Device for 4P RCCBs with Id assessment for 300mA Idn
9 | COMM1_RS485 | Communication Module (accessory) with Modbus RTU on RS485
10 | COMM2_WiFi | Communication Module (accessory) with Wi-Fi

## Event type details
Event type ID | Details
0 | Breaker close
1 | Breaker opening
2 | Breaker trip
3 | Power fail
4 | MOD/ARI/ARH upgrade
5 | COMM upgrade